DAMAGE MODELING · WORKED REFERENCE

Hail × Solar — building the curve, step by step

How the hail × solar damage curve is built across the seven stages: what we do at each stage, why, and the evidence behind every decision — with the actual sources and links.

Cell:  hail_solar      Primary damage code:  HAIL_SOLAR_PV_MODULE_V1

Primary failure-unit:  PV_MODULE_GLASS_CELL   inside PV_ARRAY

Status:  public-source-derived v1 curve — not private-claims-calibrated. This companion mirrors the seven build stages taught in the deck; the source of truth is the derivation dossier (linked at the end).

Where to find more

GitHub repo:  aamani-ai/Damage_Modeling

Derivation dossier:  hail_solar_curve_derivation_dossier_v1_3.md

Curation notebook:  notebooks/hail/solar/00_curve_curation_walkthrough.ipynb

Runtime artifact:  hail_solar__model_v1_0__docs_r5__curve_artifact.json

Slide deck:  Damage Modeling — From the Basics (Google Slides)

# STAGE 0   The modeling question

Decisive question:  What exactly are we building a curve for — and for which thing that fails?

The curve is defined before any math. We are not asking hail size → whole-plant loss %. We are asking hail diameter → the replacement damage ratio of one failure-unit: the PV module glass/cell.

NOT:   hail diameter  ->  whole solar plant damage ratio

YES:   MESH hail diameter (mm)  ->  PV_MODULE glass/cell replacement DR

Why this framing: hail damage concentrates on the exposed module glass/cells. Other subsystems (inverter, substation, racking, civil, foundation) are reviewed, but they are not forced into weak nonzero curves unless a distinct, material, sourceable direct-hail mechanism exists. Getting the failure-unit right is what keeps the whole downstream loss honest.

Reference:  03 · failure-unit coverage standard; solar-specific pathways — DOE/FEMP hail mitigation

# STAGE 1   Evidence

Decisive question:  What does the curated evidence base authorize the curve to claim — and how strong is each piece?

Before searching, we know we need five specific things — not a generic “solar hail curve”:

- what hazard intensity belongs on the x-axis

- what physical failure defines the y-axis

- at what hail sizes modules start breaking (the curve shape)

- which module types are more fragile or more resistant (selectors)

- what event-time states change damage, e.g. tracker stow (conditioners)

Four evidence classes feed the curve, each with a different role and strength (T1 = direct empirical → T4 = expert judgment / placeholder):

| Source | How it is used | Tier |
| --- | --- | --- |
| NOAA/NCEI Storm Events FAQ | Operational hazard data — fixes the x-axis and its units (hail size in inches / mm). Strong for the axis, silent on damage. | axis |
| NOAA/NWS WDTD MESH | Confirms hazard products report maximum hail size (MESH), so the axis is diameter, not energy. | axis |
| DOE/FEMP Hail Damage Mitigation for PV | Standards / qualification: IEC 61215 hail-test table — the near-zero 25 mm boundary anchor and the diameter→mass/velocity bridge. | T2 |
| PVEL 2023 Hail Stress Sequence | Lab aggregate breakage: the main archetype breakage anchors (the strongest public curve evidence). | T2 |
| Kiwa PVEL Hail Stress Sequence (current / 2024) | Additional public breakage anchors for glass//glass and thicker-glass modules. | T2/T3 |
| NREL Extreme Weather & PV Performance | Field context: latent cracking vs glass-breakage seam. Validation & caveat, not a refit anchor. | T3 |

Binding rule: field/claims evidence (NREL, VU Amsterdam 2024, Ha et al. 2020) informs direction and caveats but is not refit into the v1 curve — it is not clean enough as universal anchors. The weakest tier used on a parameter gates which metrics are honest downstream.

Reference:  08 · evidence, provenance & links standard

# STAGE 2   Grain

Decisive question:  At what level is the curve written, and what happens to everything else on the plant?

One primary nonzero curve at the failure-unit PV_MODULE_GLASS_CELL. Every other subsystem is explicitly reviewed and recorded — immune is not the same as ignored.

| Subsystem | v1 treatment | Reason |
| --- | --- | --- |
| PV_ARRAY / PV_MODULE | primary nonzero curve | Direct impact mechanism and material value. |
| MOUNTING / TRACKER | conditioner-only | Stow/angle changes module exposure; direct steel hail damage is secondary. |
| RACKING_STRUCTURE | secondary / open | Possible in extremes; not a first-order public-source curve. |
| INVERTER_SYSTEM · SUBSTATION | DR ≈ 0 (direct hail, v1) | Enclosed electrical equipment, not directly exposed like modules. |
| SCADA / MET_STATION | optional secondary | Exposed instruments can be hit, but low materiality. |
| CIVIL / FOUNDATION / DRAINAGE | DR ≈ 0 (direct hail, v1) | Direct hail does not normally drive civil/foundation replacement. |

Composition rule when more than one unit is nonzero: capex-weighted summation, each unit capped at its own saturation — sum, don’t group.

Reference:  03 · failure-unit coverage standard

# STAGE 3   Axis

Decisive question:  What variable indexes damage for the module failure-unit?

The operational x-axis is HAIL_DIAMETER_MESH_EQUIV — maximum hail diameter / MESH-equivalent, internal unit mm (source-native inches or mm allowed). Reason: hazard catalogs and operational hail products report hail size, not kinetic energy.

Kinetic energy is kept as a derived physics bridge (from the DOE/FEMP IEC hail-test table), used to interpret lab tests — not as the required input axis:

impact energy = 0.5 x mass(D) x velocity(D)^2

mass_g(D)       = 0.0005290357 x D^2.973997

velocity_mps(D) = 4.812461 x D^0.486643

| Source | How it is used | Tier |
| --- | --- | --- |
| NOAA/NCEI Storm Events FAQ | Hail magnitude reported as size in inches/hundredths — justifies a diameter axis. | axis |
| NOAA/NWS WDTD MESH | MESH estimates maximum hail size; base unit mm — the operational axis. | axis |
| DOE/FEMP (IEC 61215 hail table) | Diameter→mass→velocity table behind the kinetic-energy bridge. | T2 |

Reference:  04 · x-axis decision standard; axis units from NOAA/NCEI + NOAA/NWS MESH

# STAGE 4   Form

Decisive question:  What shape does the curve take, and what does the y-axis mean?

Form: a bounded logistic in hail diameter.

P_break(D) = 1 / (1 + exp(-k * (D - D50)))

D50 = diameter at 50% replacement/breakage probability

k   = steepness of the low-to-high transition

Why logistic: bounded in [0,1]; monotone in hail size; threshold-like without an artificial step; fits sparse public anchors without overfitting; and easy to shift horizontally for vulnerability selectors. It is a controlled v1 functional form, not a claim that nature is exactly logistic.

## What the y-axis means

The curve outputs P_break(D), and v1 uses module replacement DR ≈ P_break(D). Glass breakage is the clearest public, observable replacement trigger. Cell cracking without glass breakage (latent degradation) is deliberately kept out of this replacement-cost curve — an open seam to recalibrate if claims data shows replacement policy differs.

Reference:  why this shape — internal 06 · curve form & adjustment standard; the monotone, bounded shape is set by the empirical breakage-vs-size anchors (PVEL/Kiwa HSS); cumulative sigmoidal forms are the established convention for fragility / vulnerability curves — lognormal-CDF in HAZUS, logistic an accepted alternative (Bull. Earthquake Eng. 2021).

# STAGE 5   Adjustments

Decisive question:  What does the curve depend on besides intensity — selector, conditioner, exposure — and how does each enter?

## Selector — module_archetype (fixed asset metadata)

The selector picks one of three archetype curves, fit from public anchors in logit space:

logit(p) = ln(p/(1-p))

k   = [logit(p2) - logit(p1)] / (D2 - D1)

D50 = D1 - logit(p1)/k

| Archetype | D50 (mm) | k (1/mm) | Tier | Anchors used |
| --- | --- | --- | --- | --- |
| Fragile thin glass//glass | 41.07 | 0.220633 | T2 | 35→18% · 40→57/43% · 45→61% · 50→89% (PVEL/Kiwa) |
| Default 3.2 mm glass//backsheet | 52.70 | 0.165912 | T2 | 25→1% (IEC boundary) · 50→39% (PVEL 2023) |
| Hail-hardened / thicker glass | 64.11 | 0.135331 | T3 | 25→0.5% (IEC) · 45→7% (PVEL/Kiwa) — tail extrapolated |

Anchor sources: PVEL 2023 HSS  ·  Kiwa PVEL HSS  ·  PVEL HSS whitepaper  ·  IEC boundary via DOE/FEMP.

## Conditioner — stow_state (event-time)

If the tracker is in hail-stow when damaging hail arrives, damage drops. v1 models it as a horizontal shift plus a small cap:

DR_stowed(D)   = 0.90 * logistic(D; D50+8mm, k)

DR (unknown)   = P(stow)*DR_stowed + (1-P(stow))*DR_unstowed

Placeholder — direction sourced, magnitude not. The +8 mm shift and ×0.90 cap are a T4 placeholder. The direction is supported by VDE Americas hail-stow memo and DOE/FEMP; high-angle automated stow is commercialized (FTC Solar 80° stow) — but no public source gives a universal numeric reduction. Replace with tracker-specific test / SCADA-confirmed event state.

Note: P(stow) is P(tracker was stowed | damaging hail arrived) — not hail frequency, return period, or EAL.

## Exposure — array_exposure_fraction (value, not fragility)

Exposure scales value hit, never module fragility: loss = DR × exposure_fraction × module value. v1 runs at full site (f = 1.0); partial / footprint exposure is a v2 item.

Reference:  07 · selector / conditioner / exposure standard; stow direction — VDE Americas · DOE/FEMP

# STAGE 6   Emit

Decisive question:  What does the curve return per event, and which metrics may honestly be built from it?

The hail × solar cell emits a scalar mean DR (module glass/cell replacement DR ≈ P_break). It does not carry within-event spread, so it cannot honestly draw a deep tail. Capability declaration that ships with the curve:

failure-unit scalar DR .............. supported

scenario loss (explicit value basis)  supported

scalar EAL ......................... conditional (needs downstream frequency + cap-binding preflight)

PML / VaR / TVaR ................... withheld (no tail distribution carried)

Withhold, not caveat: a scalar curve over the event set still gives an honest expected loss; a scalar tail would be understated, so the curve declines to emit it rather than shipping it wrong.

Reference:  21 · capability & cap-binding standard; 09 · damage-code interface standard

# STAGE 7   Ship

Decisive question:  What does the consumer receive, and on what terms?

The canonical runtime artifact is hail_solar__model_v1_0__docs_r5__curve_artifact.json. The consumer (Hazard M3) pins the cell-damage-model version (v1.0) and calls it; the dossier + source context ship with it.

## Value linkage stays separate

loss_$ = DR_module(D) x physical_base_$ x PV_ARRAY_value_share

x f_hail_material_share x array_exposure_fraction

Keeping these factors separate is what prevents module damage from being applied to the whole project TIV.

## Reviewer checklist (before use)

- x-axis is diameter / MESH, not unlabeled kinetic energy

- module archetype known, or defaulted with a flag

- stow state known, or probabilistic stow clearly labeled (not confused with hail frequency)

- exposure_fraction site-specific or explicitly full-site default

- curve applied only to PV_MODULE / PV_ARRAY exposed value, never whole TIV

- tail / EAL handled downstream with hazard frequency + uncertainty, not inside this damage code

## What makes v2 better (replace placeholders, not polish)

- BOM-specific hail test reports → exact curve parameters (replaces archetypes)

- claims / repair-policy calibration → calibrate P_break to actual replacement DR

- tracker/stow-angle testing → replace the +8 mm / ×0.90 placeholder

- SCADA/event logs → replace assumed P(stow) with observed state

- site MESH swath overlay → replace exposure_fraction = 1.0 default

Reference:  09 · damage-code interface standard

# REFERENCES   All sources used, with links

| Source | What it supports | Tier | Link |
| --- | --- | --- | --- |
| NOAA/NCEI Storm Events FAQ | Hail reported as size (in/mm) — the axis | axis | open ↗ |
| NOAA/NWS WDTD MESH | Max hail size (MESH) — operational axis | axis | open ↗ |
| DOE/FEMP Hail Damage Mitigation for PV | IEC 61215 boundary + diameter→mass/velocity bridge; stow direction | T2 | open ↗ |
| PVEL 2023 Hail Stress Sequence | Default & fragile breakage anchors | T2 | open ↗ |
| Kiwa PVEL current HSS | glass//glass & thicker-glass anchors | T2/T3 | open ↗ |
| Kiwa PVEL 2024 HSS | Updated public breakage anchors | T2/T3 | open ↗ |
| PVEL Hail Stress Sequence whitepaper | HSS methodology & field-informed context | T2/T3 | open ↗ |
| NREL Extreme Weather & PV Performance | Latent-cracking vs glass-breakage seam (caveat) | T3 | open ↗ |
| VDE Americas hail-stow memo | Direction of stow benefit | T4 | open ↗ |
| FTC Solar 80° hail-stow announcement | High-angle stow is commercialized | T4 | open ↗ |

Source of truth on GitHub: hail_solar dossier v1.3  ·  curation notebook  ·  method standards  ·  slide deck.