## README
field | value
cell_id | winter_storm_solar
model | model v0.1 / docs r1 (proposed, not indexed)
grade | screening_engineering_proxy
runtime artifact | docs/cells/winter_storm_solar/proposed/winter_storm_solar__model_v0_1__docs_r1__curve_artifact.json
note | Derivation/audit view only; the JSON artifact is the runtime object.

## Structure_Curve
event_to_design_ratio | DR_lower_resistance | DR_central_screening | DR_upper_resistance
0 | 0 | 0 | 0
0.1 | 1.3397e-07 | 9.2944e-09 | 9.6324e-11
0.2 | 0.0001107 | 1.5091e-05 | 4.4905e-07
0.3 | 0.0022166 | 0.00044384 | 2.4158e-05
0.4 | 0.012398 | 0.0032383 | 0.00026827
0.5 | 0.037658 | 0.012021 | 0.0013708
0.6 | 0.081086 | 0.030349 | 0.0044699
0.7 | 0.14098 | 0.060119 | 0.010943
0.8 | 0.21271 | 0.10117 | 0.022035
0.9 | 0.2908 | 0.15175 | 0.038576
1 | 0.37034 | 0.20927 | 0.060879
1.1 | 0.44756 | 0.27097 | 0.088763
1.2 | 0.51993 | 0.33428 | 0.12166
1.3 | 0.586 | 0.39707 | 0.15876
1.4 | 0.64512 | 0.45775 | 0.19911
1.5 | 0.69722 | 0.51519 | 0.24174
1.6 | 0.74259 | 0.56865 | 0.28573
1.7 | 0.78176 | 0.61778 | 0.33023
1.8 | 0.81533 | 0.66245 | 0.37453
1.9 | 0.84395 | 0.7027 | 0.41804
2 | 0.86825 | 0.73873 | 0.46027
2.1 | 0.88882 | 0.7708 | 0.50088
2.2 | 0.90619 | 0.7992 | 0.53959
2.3 | 0.92083 | 0.82427 | 0.57625
2.4 | 0.93317 | 0.84633 | 0.61075
2.5 | 0.94355 | 0.86569 | 0.64304
2.6 | 0.95228 | 0.88264 | 0.67314
2.7 | 0.95963 | 0.89747 | 0.70108
2.8 | 0.96582 | 0.91043 | 0.72693
2.9 | 0.97103 | 0.92174 | 0.75077
3 | 0.97542 | 0.93161 | 0.77272
3.1 | 0.97912 | 0.94021 | 0.79287
3.2 | 0.98224 | 0.94771 | 0.81133
3.3 | 0.98488 | 0.95424 | 0.82823
3.4 | 0.98711 | 0.95994 | 0.84367
3.5 | 0.989 | 0.96491 | 0.85776
3.6 | 0.9906 | 0.96924 | 0.8706
3.7 | 0.99195 | 0.97302 | 0.88231
3.8 | 0.99311 | 0.97632 | 0.89296
3.9 | 0.99409 | 0.9792 | 0.90265
4 | 0.99492 | 0.98171 | 0.91146

## Module_Direct_Curve
array_snow_load_kpa | direct_DR_lower | direct_DR_central | direct_DR_upper
0 | 0 | 0 | 0
0.2 | 2.2204e-16 | 0 | 0
0.4 | 4.0199e-08 | 1.0997e-10 | 4.89e-13
0.6 | 9.0422e-05 | 1.1514e-06 | 1.7769e-08
0.8 | 0.0047482 | 0.00017569 | 6.4742e-06
1 | 0.044465 | 0.003664 | 0.00026178
1.2 | 0.16558 | 0.025453 | 0.0030802
1.4 | 0.36123 | 0.090828 | 0.016897
1.6 | 0.57101 | 0.21141 | 0.056099
1.8 | 0.74218 | 0.37054 | 0.13194
2 | 0.85803 | 0.53626 | 0.24327
2.2 | 0.92685 | 0.68163 | 0.37654
2.4 | 0.96413 | 0.79398 | 0.51335
2.6 | 0.98304 | 0.87296 | 0.6382
2.8 | 0.99218 | 0.92463 | 0.74218
3 | 0.99646 | 0.95663 | 0.82279
3.2 | 0.99842 | 0.97564 | 0.88183
3.4 | 0.9993 | 0.98657 | 0.92317
3.6 | 0.99969 | 0.9927 | 0.95107
3.8 | 0.99986 | 0.99607 | 0.96937
4 | 0.99994 | 0.99791 | 0.98109
4.2 | 0.99997 | 0.99889 | 0.98845
4.4 | 0.99999 | 0.99941 | 0.99301
4.6 | 0.99999 | 0.99969 | 0.9958
4.8 | 1 | 0.99984 | 0.99749
5 | 1 | 0.99991 | 0.99851
5.2 | 1 | 0.99995 | 0.99911
5.4 | 1 | 0.99998 | 0.99948
5.6 | 1 | 0.99999 | 0.99969
5.8 | 1 | 0.99999 | 0.99982
6 | 1 | 1 | 0.99989

## Rack_Tests
source_id | specimen | design_pa | failure_pa | failure_over_design
WSS-S022 | i steel 4x2 | 1294 | 4250 | 3.28
WSS-S022 | ii steel 4x4 | 1294 | 1750 | 1.35
WSS-S022 | iii aluminium 4x5 | 1036 | 1000 | 0.97
WSS-S022 | iv aluminium+steel 4x5 | 1036 | 2250 | 2.17
WSS-S022 | v aluminium+steel 4x6 | 688 | 2000 | 2.91
WSS-S022 | vi steel scaffold pipe 4x4 | 1036 | 1250 | 1.21
WSS-S023 | JSME thin-wall steel truss | 1980 | 5038 | 2.5444

## Value_Crosswalk
value_source_id | source_location | row_or_bucket_id | row_or_bucket_label | value | unit | financial_class | failure_unit_id | applicable_pathway_ids | role_in_loss | include_in_direct_denominator | allocation_rule | double_count_guardrail | status | notes
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!2 | SOLAR_VALUE_002_MODULE | Module hardware + module-level | 291.21485143992487 | 2024_USD_per_kWdc | direct_hardware | WSS1_MODULE_FIELD_BREAKAGE | snow_gravity_load | direct_vulnerable_value | true | Same-unit denominator; site value overrides. | Do not charge module loss again after the cascade. | mapped_reference_only
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!3 | SOLAR_VALUE_003_MOUNTING | SBOS tracker/racking hardware | 109.98972602739727 | 2024_USD_per_kWdc | direct_hardware | WSS1_SUPPORT_STRUCTURE_COLLAPSE | snow_gravity_load | direct_vulnerable_value | true | Same-unit denominator excluding piles; site value overrides. | Do not include foundation or SBOS labour. | mapped_reference_only
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!4 | SOLAR_VALUE_004_FOUNDATION | SBOS driven piers + EBOS pad | 31.12448715327472 | 2024_USD_per_kWdc | direct_hardware | WSS1_FOUNDATION | snow_gravity_load | withheld | true | Withheld; no snow-load foundation curve. | Frost heave and settlement are other pathways. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!5 | SOLAR_VALUE_005_INVERTER | Central inverter hardware | 32.306366410372384 | 2024_USD_per_kWdc | direct_hardware | WSS1_POWER_CONVERSION_AND_ELECTRICAL | snow_gravity_load | withheld | true | Withheld. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!6 | SOLAR_VALUE_006_COMBINER | EBOS combiner boxes | 6.82625 | 2024_USD_per_kWdc | direct_hardware | WSS1_POWER_CONVERSION_AND_ELECTRICAL | snow_gravity_load | withheld | true | Withheld. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!7 | SOLAR_VALUE_007_CABLING | EBOS conductors | 69.3201119402985 | 2024_USD_per_kWdc | direct_hardware | WSS1_POWER_CONVERSION_AND_ELECTRICAL | snow_gravity_load | withheld | true | Withheld. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!8 | SOLAR_VALUE_008_SUBSTATION | EBOS transformer/switches/breakers/substation | 106.50466417910448 | 2024_USD_per_kWdc | direct_hardware | WSS1_POWER_CONVERSION_AND_ELECTRICAL | snow_gravity_load | withheld | true | Withheld; ice on yard equipment is another pathway. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!9 | SOLAR_VALUE_009_GROUNDING | EBOS grounding / lightning | 8.385 | 2024_USD_per_kWdc | direct_hardware | WSS1_POWER_CONVERSION_AND_ELECTRICAL | snow_gravity_load | withheld | true | Withheld. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!10 | SOLAR_VALUE_010_SCADA | EBOS system monitor | 1.31 | 2024_USD_per_kWdc | direct_hardware | WSS1_SCADA_COMMUNICATIONS | snow_gravity_load | withheld | true | Withheld. | None charged. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!11 | SOLAR_VALUE_011_NETWORK_UPGRADE | Grid network upgrade | 38.253731343283576 | 2024_USD_per_kWdc | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | snow_gravity_load | excluded | false | Excluded nonphysical. | Never in the physical denominator. | mapped
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!12 | SOLAR_VALUE_012_SBOS_LABOR | SBOS field labor | 43.273972602739725 | 2024_USD_per_kWdc | support_logistics | WSS1_REPLACEMENT_SUPPORT | snow_gravity_load | support_once | false | Part of the 189.59 support pool; allocated once. | No independent DR. | mapped
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!13 | SOLAR_VALUE_013_EBOS_LABOR | EBOS field labor | 39.447761194029844 | 2024_USD_per_kWdc | support_logistics | WSS1_REPLACEMENT_SUPPORT | snow_gravity_load | support_once | false | Part of the 189.59 support pool; allocated once. | No independent DR. | mapped
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!14 | SOLAR_VALUE_014_SITE_PREP | Fieldwork site prep | 31.223744292237445 | 2024_USD_per_kWdc | civil | WSS1_CIVIL_INFRA | snow_gravity_load | withheld | false | Withheld civil. | Not in the support pool. | withheld
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!15 | SOLAR_VALUE_015_SITE_MANAGEMENT | Site management, equipment rental | 106.86876712328767 | 2024_USD_per_kWdc | support_logistics | WSS1_REPLACEMENT_SUPPORT | snow_gravity_load | support_once | false | Part of the 189.59 support pool; allocated once. | No independent DR. | mapped
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!16 | SOLAR_VALUE_016_OFFICEWORK | PVSCM officework total | 70.27756559667417 | 2024_USD_per_kWdc | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | snow_gravity_load | excluded | false | Excluded soft cost. | Never in the physical denominator. | mapped
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!17 | SOLAR_VALUE_017_OTHER | PVSCM other total | 133.6730006973752 | 2024_USD_per_kWdc | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | snow_gravity_load | excluded | false | Excluded soft cost. | Never in the physical denominator. | mapped

## Parameter_Tiers
parameter | pathway_id | curve_id | value | param_role | tier | source_ids | reasoning | status | update_trigger
pathway_id | all_shared | ALL | snow_gravity_load; no default | axis_bridge | T4_placeholder_or_expert_judgment | WSS-S019 | Pathway identity is required. | adopt | Governed pathway redesign.
swe_to_kpa | snow_gravity_load | ALL | 0.00980665 kPa per mm SWE | axis_bridge | T2_public_lab_standard_or_physics | WSS-S031 | Physics of water-equivalent mass. | adopt | None.
glaze_kpa_per_mm_radial | snow_gravity_load | ALL | pi x 0.9 x 0.00980665 = 0.027726 | axis_bridge | T2_public_lab_standard_or_physics | WSS-S031 | No-wind Simple-model identity; conservative with wind. | adopt | Flat-surface glaze product.
flat_roof_factor | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.7 | axis_bridge | T2_public_lab_standard_or_physics | WSS-S002 | ASCE 7-22 Eq 7.3-1 (secondary). | adopt | ASCE 7-22 text.
exposure_factor_ce | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.9 | selector_default | T3_engineering_proxy_or_adjacent_empirical | WSS-S025 | Practitioner ground-mount calc. | adopt | Site exposure.
thermal_factor_ct | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 1.2 | selector_default | T3_engineering_proxy_or_adjacent_empirical | WSS-S025 | Unheated array. | adopt | ASCE 7-22 text.
default_slope_factor_cs | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 1.0 | conditioner_adjustment | T4_placeholder_or_expert_judgment | WSS-S006;WSS-S025 | No slope credit without verified clearance/stow. | adopt | Verified clearance and stow evidence.
structure_beta_ln | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 0.47 | curve_fit_shape | T2_public_lab_standard_or_physics | WSS-S022;WSS-S023 | Log-sd of seven measured failure/design ratios. | adopt | More tests.
structure_DS1_median_lower | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 1.05 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S022;WSS-S023;WSS-S019 | 1.88 x 0.56 (test design = old 50-yr nominal). | adopt | US test vs ASCE 7-22.
structure_DS1_median_central | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 1.32 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S022;WSS-S023;WSS-S002 | 1.88 x 0.7 (ASD design to 0.7 pg). | adopt | US test vs ASCE 7-22.
structure_DS1_median_upper | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 1.88 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S022;WSS-S023 | Test design taken as pg. | adopt | US test vs ASCE 7-22.
structure_DS2_to_DS1_median_ratio | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 1.2 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S023;WSS-S014 | Brittle collapse after first buckling. | adopt | Buckling-to-collapse load data.
structure_DS1_cost_ratio | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 0.40 | exposure_or_value | T3_engineering_proxy_or_adjacent_empirical | WSS-S030 | ~37% case. | adopt | Larger case set.
structure_DS2_cost_ratio | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 1.00 | exposure_or_value | T3_engineering_proxy_or_adjacent_empirical | WSS-S030 | ~80% and total-collapse cases. | adopt | Larger case set.
structure_axis_valid_range | snow_gravity_load | WSS1_SUPPORT_STRUCTURE_ORDERED_STATES | 0.0-4.0; flag above 3.3 | extrapolation_guard | T4_placeholder_or_expert_judgment | WSS-S022 | Highest tested ratio 3.28. | adopt | Tests at higher ratios.
module_beta_ln | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.25 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S011;WSS-S010 | Spread across BOMs. | adopt | Snow-specific TtF data.
module_capacity_lower_central_upper_kpa | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 1.8 / 2.3 / 2.8 (before knock-down) | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | WSS-S011;WSS-S010 | Modern TtF range. | adopt | Snow-specific TtF data.
lower_edge_knockdown | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.85 | curve_fit_shape | T4_placeholder_or_expert_judgment | WSS-S003;WSS-S006;WSS-S016 | Non-uniform lower-edge load. | adopt | IEC 62938 table / AIST values.
module_DS1_cost_ratio | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 1.00 | exposure_or_value | T4_placeholder_or_expert_judgment | WSS-S030;WSS-S028 | Broken modules are replaced. | adopt | Repair-vs-replace data.
module_axis_valid_range | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.0-6.0 kPa; flag above 4.5 | extrapolation_guard | T4_placeholder_or_expert_judgment | WSS-S011 | About 1.6 x highest TtF. | adopt | Higher-capacity module data.
cascade_central_nonsalvage | snow_gravity_load | WSS1_MODULE_FIELD_DIRECT_ORDERED_STATES | 0.8 (bounds 0.0, 1.0) | conditioner_adjustment | T4_placeholder_or_expert_judgment | WSS-S030;WSS-S028 | Modules on collapsed rows mostly lost. | adopt | Salvage records.
snow_stow_credit | snow_gravity_load | ALL | none | conditioner_adjustment | T4_placeholder_or_expert_judgment | WSS-S018 | No efficacy evidence. | adopt | Stow efficacy data.
support_allocation_rule | snow_gravity_load | WSS1_REPLACEMENT_SUPPORT | pool 189.59 x direct loss / 656.98 | exposure_or_value | T4_placeholder_or_expert_judgment | WSS-S032 | Allocate once after direct damage. | adopt | Qualified support-cost data.

## Claim_Register
claim_id | pathway_id | claim_text | claim_type | source_ids | exact_locator | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
WSS-C001 | snow_gravity_load | Winter storm bundles distinct mechanisms; v0.1 governs the snow (+ glaze weight) gravity-load pathway only. | governance_decision | WSS-S019;WSS-S029 | DECISION_LOG D1-D4 | T4_placeholder_or_expert_judgment | pathway_id=snow_gravity_load; deferred: ice_with_concurrent_wind, ice_shedding_impact, snow_drift_and_sliding_impact | adopt | Govern snow (+glaze) gravity load as the v0.1 primary pathway; other winter mechanisms are separate. | Default any winter mechanism to this pathway. | JL checkpoint-1 decision; standard 18 split. | A governed winter pathway redesign.
WSS-C002 | snow_gravity_load | 1 mm of snow water equivalent is 1 kg/m2, i.e. 9.80665 Pa of ground load. | direct_observation | WSS-S031 | p.5 Eq.(1) | T2_public_lab_standard_or_physics | load_bridge.swe_to_kpa=0.00980665 per mm | adopt | Convert SWE to areal load without a density assumption. | Converting snow depth without measured density. | Water-equivalent depth fixes mass per area by definition. | None expected (physics).
WSS-C003 | snow_gravity_load | Glaze weight on a flat surface is approximately pi x rho_i x equivalent radial ice thickness x g. | source_interpretation | WSS-S031 | p.5 Eq.(1); p.6 | T2_public_lab_standard_or_physics | load_bridge.glaze_kpa_per_mm=pi*0.9*0.00980665 | adopt | Add glaze weight on flat surfaces as pi x 0.9 x radial thickness of water. | Treating the identity as exact when wind-driven accretion contributes. | With no wind the Simple model gives Req = P/(pi rho_i); flat accumulation equals P; with wind the identity overstates. | A flat-surface glaze measurement product from the hazard grid.
WSS-C004 | snow_gravity_load | Array snow load follows ASCE 7-22 pf = 0.7 Ce Ct pg with slope reduction lost when the leading edge is buried. | source_interpretation | WSS-S001;WSS-S002;WSS-S025 | article bodies; calc pp.7-8 | T3_engineering_proxy_or_adjacent_empirical | load_bridge: pf = 0.7 Ce Ct pg; Ce 0.9, Ct 1.2 defaults; Cs default 1.0 | adopt | Bridge ground load to array load for the module axis; no slope credit by default. | Applying a slippery-surface Cs credit without verified clearance/stow. | ASCE 7-22 Eq 7.3-1 via secondary sources; practitioner calc shows Ce/Ct choices and Cs loss at low clearance. | ASCE 7-22 Ch.7 text or the ASCE 2025 ground-mount book.
WSS-C005 | snow_gravity_load | In ASCE 7-22 the mapped ground snow load is a strength-level value (load factor 1.0). | source_interpretation | WSS-S001 | article body | T2_public_lab_standard_or_physics | axis semantics: r = 1 at the ASCE 7-22 strength-level design load | adopt | Define the structure axis against the strength-level pg. | A return period for a site from r. | ASCE 7-22 ground snow loads are strength-level with load factor 1.0. | ASCE 7-22 text verification.
WSS-C006 | snow_gravity_load | Seven full-scale ground-mount racks failed at 0.97-3.28 times their design pressure (median 1.88, log-sd 0.47). | direct_observation | WSS-S022;WSS-S023 | Table D5; Sec 3 + Table 3 | T2_public_lab_standard_or_physics | structure capacity ratios {3.28,1.35,0.97,2.17,2.91,1.21,2.54}; lognormal median 1.88, beta 0.47 | adopt | Anchor the support-structure capacity spread and median relative to manufacturer design. | Treating n=7 Japanese fixed-tilt racks as a calibrated population fragility. | Full-scale tests measured collapse load / design load directly. | More full-scale tests or US forensic data.
WSS-C007 | snow_gravity_load | The test design load maps onto the ASCE 7-22 axis with an unresolved factor between about 0.56 and 1.0. | engineering_inference | WSS-S019;WSS-S001;WSS-S022 | Sec.1; article; Table D5 | T4_placeholder_or_expert_judgment | capacity_scenarios medians r = 1.05 / 1.32 / 1.88 (DS1) | adopt | Carry three unweighted resistance scenarios for the Japanese-to-ASCE design-load mapping. | Presenting scenarios as percentiles or a calibrated distribution. | Test design pressure maps to ASCE 7-22 r via 1/1.8 (old 50-yr nominal), 0.7 (ASD) or 1.0; mapping unverified. | A US full-scale test against ASCE 7-22 design loads.
WSS-C008 | snow_gravity_load | Japanese reported snow events damaged about 37%, about 80%, and 100% of the affected arrays. | direct_observation | WSS-S030;WSS-S021 | p.4 cases 2-4; p.2 Fig.5 | T1_claims_or_field_calibrated | damage_state cost ratios DS1 0.40, DS2 1.00 | adopt | Set partial (~37%) and extensive (~80% to total) collapse states. | Per-plant damage rates. | Regulator cases report per-event damaged share once snow exceeded design. | A larger case set with load data.
WSS-C009 | snow_gravity_load | Rack collapse is brittle: global collapse follows first member buckling closely. | engineering_inference | WSS-S023;WSS-S014 | Sec 3; abstract | T4_placeholder_or_expert_judgment | DS2 median = 1.2 x DS1 median | adopt | Keep extensive collapse close to collapse onset (brittle buckling). | Treating 1.2 as measured. | Post buckling was followed immediately by global collapse; cold-formed members have little reserve. | Tests reporting the load gap between first buckling and full collapse.
WSS-C010 | snow_gravity_load | Modern large-format tracker modules fail at about 1.8-2.8 kPa uniform downforce. | source_interpretation | WSS-S011;WSS-S010;WSS-S009 | article results; MSS results | T3_engineering_proxy_or_adjacent_empirical | module direct capacity scenario medians 1.8 / 2.3 / 2.8 kPa before knock-down; beta 0.25 (T4) | adopt | Place module breakage on absolute array load. | A BOM-specific capacity. | Lab test-to-failure populations and MSS failures bound modern module capacity. | Snow-specific module TtF data.
WSS-C011 | snow_gravity_load | Snow concentrates at the module lower edge, below the uniform-test capacity. | engineering_inference | WSS-S003;WSS-S006;WSS-S016 | scope; slides; poster | T4_placeholder_or_expert_judgment | lower_edge_knockdown = 0.85 | adopt | Reduce module capacity for lower-edge snow concentration. | Treating 0.85 as measured. | Lower-edge loading is measured as concentrated but no factor is published. | IEC 62938 load table or AIST eave-load values.
WSS-C012 | snow_gravity_load | Modules on collapsed racking are mostly lost; modules can also fail without racking damage. | engineering_inference | WSS-S030;WSS-S028 | case 1; slide 15 | T4_placeholder_or_expert_judgment | module_structure_cascade: central nonsalvage 0.8; bounds 0.0 and 1.0 | adopt | Make modules on collapsed rows mostly nonsalvageable, once. | Charging module loss twice. | Collapsed racks dropped or broke modules; module-only state exists separately. | Field salvage records.
WSS-C013 | snow_gravity_load | Tracker snow capacity is a project choice (5 psf standard, up to 60 psf). | direct_observation | WSS-S012;WSS-S026 | spec table; snippet | T2_public_lab_standard_or_physics | racking_design_basis selector: site_code_assumed ¦ project_rated | adopt | Require a declared design basis; screening assumes site code. | Assuming a tracker meets site code without stating it. | Trackers ship at 5 psf standard unless configured up. | Verified tracker datasheets.
WSS-C014 | snow_gravity_load | Snow stow and snow removal can reduce load but have no published efficacy. | governance_decision | WSS-S018;WSS-S007 | page body; guidance | T4_placeholder_or_expert_judgment | snow_stow_state numeric effect: none | adopt | Capture stow and snow removal; no numeric credit. | Crediting stow or removal without efficacy evidence. | Unknown mitigation receives no credit (pressure-test checklist). | Stow efficacy field data.
WSS-C015 | snow_gravity_load | Real snow collapses are dominated by racks designed or built below the required load. | direct_observation | WSS-S021;WSS-S030;WSS-S013;WSS-S019 | releases; article; preface | T1_claims_or_field_calibrated | capacity spread includes design deficiency (beta 0.47; lower scenario) | adopt | Represent under-design through the measured spread and the lower scenario, not a separate multiplier. | A separate deficiency multiplier on top of the measured spread. | Field collapses are dominated by under-design; the tested sample already includes weak racks. | Population data on as-built design compliance.
WSS-C016 | snow_gravity_load | Single-axis tracker snow capacity is not directly tested in the located evidence. | unresolved_hypothesis | WSS-S004;WSS-S012;WSS-S018 | articles; specs | T3_engineering_proxy_or_adjacent_empirical | tracker transfer flag TRACKER_TRANSFER_FROM_FIXED_RACK_TESTS | adopt | Apply the structure curve to trackers only as a flagged transfer. | Claiming tracker-specific calibration. | All tested racks are fixed-tilt; tracker torque tubes, drives and stow differ. | Tracker full-scale snow tests.
WSS-C017 | snow_gravity_load | Module (291.21) and racking (109.99) rows are the direct vulnerable value for this pathway. | governance_decision | WSS-S032 | Solar_Map rows 2-17 | T2_public_lab_standard_or_physics | value crosswalk and support allocation rule | adopt | Map module and structure rows as direct value; support pool allocated once. | Support rows receiving their own DR. | Row-level reconciliation to 877.80 physical and 1120 installed. | Updated value workbook.
WSS-C018 | snow_gravity_load | No located evidence supports a snow-load curve for foundations, electrical, SCADA, or civil units. | governance_decision | BOUNDED_SEARCH_LOG | search log Secs 2-4 | T4_placeholder_or_expert_judgment | withheld: foundation, power conversion/electrical, SCADA, civil | withhold | Withhold units without snow-load response evidence. | Reading withheld as undamaged. | No located evidence links snow load to these units' replacement cost at this grain. | Unit-specific snow damage evidence.
WSS-C019 | snow_gravity_load | No public claims data located for snow losses on US PV. | direct_observation | BOUNDED_SEARCH_LOG | search log Sec 4 | T4_placeholder_or_expert_judgment | insurance snow share: not located | withhold | Record the claims gap. | Asserting snow is immaterial in claims. | No snow-specific share located in GCube, kWh Analytics or AXIS public material. | kWh Analytics / GCube full reports (JL).

## Source_Register
source_id | citation | url | accessed_on | exact_locator | source_type | source_role | pathway_ids | evidence_tier | target_asset_match | target_failure_unit_match | measured_or_modeled_endpoint | permitted_inference | prohibited_inference | decision | status | notes
WSS-S001 | STRUCTURE magazine, 'Snow and Rain Loads in ASCE 7-22'. | https://www.structuremag.org/article/snow-and-rain-loads-in-asce-7-22/ | 2026-10-12 | article body | standard commentary (secondary to ASCE/SEI 7-22) | axis_bridge | snow_gravity_load | T2_public_lab_standard_or_physics | none | none | ground snow load map basis and load factor | ASCE 7-22 ground snow loads are reliability-targeted strength-level values; snow load factor 1.6 -> 1.0. | Exact ASCE wording, a site return period, or any damage probability. | adopt | reviewed | Standard text paywalled; JL to obtain ASCE 7-22 Ch.7 to verify.
WSS-S002 | STRUCTURE magazine, 'ASCE 7-22 Flat Roof Snow Load versus Minimum Snow Load'. | https://www.structuremag.org/article/asce-7-22-flat-roof-snow-load-versus-minimum-snow-load/ | 2026-10-12 | Eq. 7.3-1; Sec 2.4.1 combinations | standard commentary (secondary) | axis_bridge | snow_gravity_load | T2_public_lab_standard_or_physics | none | none | flat roof snow load and load combinations | pf = 0.7 Ce Ct pg; strength 1.2D + 1.0S; ASD D + 0.7S. | A PV slope factor value or a resistance level. | adopt | reviewed | Verify in ASCE 7-22 text (JL).
WSS-S003 | IEC 62938:2020 ed.1, PV modules - Non-uniform snow load testing (official VDE preview). | https://assets.vde-verlag.de/iec-normen/preview-pdf/info_iec62938%7Bed1.0%7Db.pdf | 2026-10-12 | Clause 1 scope/introduction | standard | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | non-uniform snow load limit of framed modules | Typical snow field failures are glass breakage and frame bending at the lower edge; uniform tests miss them. | Any numeric non-uniform load limit (beyond preview; paywalled). | adopt | reviewed
WSS-S004 | Cao A., 'Beyond IEC 61215-2: rethinking mechanical testing for tracker-mounted PV modules', PV Tech, 2026-03-27. | https://www.pv-tech.org/beyond-iec-61215-2-rethinking-mechanical-testing-for-tracker-mounted-pv-modules/ | 2026-10-12 | article body | trade press by structural engineer | mechanism_only | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | partial | partial | tracker clamp demand vs IEC fixture (wind) | Tracker clamp geometry raises module demand relative to the IEC test fixture. | Snow-specific capacity numbers (article is wind-focused). | adopt | reviewed
WSS-S005 | Sinovoltaics learning centre, 'IEC 61215 MQT 16 static mechanical load test' (secondary to IEC 61215-2:2021). | https://sinovoltaics.com/learning-center/testing/iec-61215-mqt-16-static-mechanical-load-test-for-solar-modules/ | 2026-10-12 | page body | secondary explainer | mechanism_only | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | direct | direct | test load = gamma_m x design load (gamma_m >= 1.5) | Datasheet 5400 Pa is a test load; passing means no failure at the test load. | Treating datasheet test loads as failure loads; using secondary text as the standard. | demote | reviewed | IEC 61215-2:2021 paywalled; JL to obtain.
WSS-S006 | Takashima T. et al. (AIST), PV safety results meeting 2019, oral T11 slides. | https://unit.aist.go.jp/rpd-envene/PV/ja/results/2019/oral/T11.pdf | 2026-10-12 | slides pp.13-15 | agency field measurement | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | partial | measured eave (lower-edge) snow load on PV arrays | A large load acts on the array lower edge; eave burial removes slope reduction (Cs = 1). | Numeric eave-load magnitudes (chart values not extractable). | adopt | reviewed
WSS-S007 | NITE, 'Points for reducing snow/ice accident risk' (attachment to 2025-11-20 release). | https://www.nite.go.jp/data/000159576.pdf | 2026-10-12 | pp.1-3 | regulator guidance | conditioner_adjustment | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | direct | partial | operational mitigation guidance | Snow removal, tilt, and clearance are real loss modifiers; eave load concentration is the failure path. | Any mitigation efficacy coefficient or damage ratio. | adopt | reviewed
WSS-S009 | Kiwa PVEL, 'PQP v12 update to better address module breakage'. | https://www.kiwa.com/pvel/pqpv12 | 2026-10-12 | page body | lab protocol | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | tracker-mounted static load to failure | Modern tracker-mounted module breakage is characterised from 1800 Pa upward; failure can be time-dependent. | Numeric failure loads (not on the page). | adopt | reviewed
WSS-S010 | Kiwa PVEL, 2024 PV Module Reliability Scorecard, Mechanical Stress Sequence. | https://2024modulescorecard.pvel.com/mechanical-stress-sequence/ | 2026-10-12 | MSS results section | lab test results | boundary_or_cap | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | MSS failures at +/-1800 Pa tracker mount | About 7% of BOMs fail some MSS step at tracker-mount +/-1800 Pa: lower-tail module failure sits well below 5400 Pa. | A snow-specific failure fraction. | adopt | reviewed
WSS-S011 | Sillerud C. (CFV Labs), 'PV modules are getting weaker: how should the industry respond?', PV Tech, 2024-09-16. | https://www.pv-tech.org/pv-modules-are-getting-weaker-how-should-the-industry-respond/ | 2026-10-12 | article body; population results | lab data reported by test lab | curve_fit_shape | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | direct | direct | module test-to-failure under uniform downforce | Modern large-format tracker modules fail at roughly 1.8-2.8 kPa uniform downforce (derived from reported reductions). | A specific BOM value; equating uniform-pressure TtF with non-uniform snow capacity. | adopt | reviewed | Medians 1,770-2,780 Pa are arithmetic on the article's percentage reductions.
WSS-S012 | NOV, TechTrack solar tracker flyer (manufacturer). | https://assets.nov.com/NCP4N68N/at/cmb5wnnmbgk5brszbkjxgth/NOV_CMKT_Solar_TechTrack_Flyer.pdf | 2026-10-12 | spec table 'Wind + Snow Load Capacity' | manufacturer specification | selector_archetype | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | tracker standard and configurable snow capacity | Utility trackers ship at a 5 psf (0.24 kPa) standard snow capacity, configurable to 60 psf: capacity is project-specific. | A snow-stow angle or efficacy. | adopt | reviewed
WSS-S013 | Alto (alto.ad), 'FEDA Dismantles Grau Roig Solar Park After Snow Damage', 2026-05-19 (+ 2026-03 report). | https://www.alto.ad/environment/2026/05/andorra-grau-roig-solar-park-collapse-flawe | 2026-10-12 | article body | press report of field event | case_study_severity | snow_gravity_load | T1_claims_or_field_calibrated | partial | direct | whole-plant snow collapse attributed to support under-design | Documented whole-plant collapse where supports were sized below regulatory loads (design deficiency mode). | Any numeric event/design ratio. | adopt | reviewed | Read via press; expert report unpublished; operator disputes.
WSS-S014 | Turer A. (METU), ACE2026 keynote abstract, forensic snow failures of Turkish solar plants. | https://ace2026.ktu.edu.tr/ACE2026_keynote_Turer.html | 2026-10-12 | abstract | forensic talk abstract | mechanism_only | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | partial | direct | failure modes | Cold-formed C-section buckling and connection failures dominate; trapped snow amplifies load. | Numbers. | adopt | reviewed
WSS-S015 | O'Rourke M. et al., 'Design Snow Loads for Ground Mounted Solar Panels', ASCE Press, 2025. | https://sp360.asce.org/PersonifyEbusiness/Merchandise/Product-Details/productId/322561249 | 2026-10-12 | press summary only | design guidance | axis_bridge | snow_gravity_load | T2_public_lab_standard_or_physics | direct | partial | ground-mount PV snow load provisions | Service-life factor, leading-edge height and partial loading matter for the ground-to-array bridge. | Any factor value (not read). | defer | unavailable | Most important missing source; paywalled; JL to obtain.
WSS-S016 | Oozeki T. et al. (AIST/NIED/universities), snow load design study for PV, AIST 2019 poster P109. | https://unit.aist.go.jp/rpd-envene/PV/ja/results/2019/poster/P109.pdf | 2026-10-12 | single page | agency field measurement | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | partial | eave settlement load on module frames | Accidents continue despite JIS C 8955; module-frame and settlement loads are the open issues. | kN/m values read off the figure. | adopt | reviewed
WSS-S017 | Romer P., Beinert A.J., 'Effects of inhomogeneous snow load on the mechanics of a PV module', 38th EU PVSEC, 2021. | https://www.ise.fraunhofer.de/content/dam/ise/de/documents/publications/conference-paper/38th-eupvsec-2021/Romer_4BO45.pdf | 2026-10-12 | Abstract; Sec.1; Sec.3 | conference paper (FEM) | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | partial | cell stress under homogeneous vs inhomogeneous load | Inhomogeneous snow is not worse for cell stress; cold raises cell-crack probability. | Frame or glass failure loads (not modelled). | adopt | reviewed
WSS-S018 | Array Technologies, 'ARRAY SmarTrack' product page (Automated Snow Response). | https://arraytechinc.com/?p=14744 | 2026-10-12 | page body | manufacturer page | conditioner_adjustment | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | snow stow feature | Tracker design can assume active snow stow to reduce structure, making capacity conditional on stow working. | A stow angle, threshold, or efficacy credit. | adopt | reviewed
WSS-S019 | NEDO/JPEA, 'Design guideline for ground-mounted PV systems, 2019 edition' (main text). | https://www.nedo.go.jp/content/100895022.pdf | 2026-10-12 | Preface p.i; Sec.1 pp.~12-13 | design guideline | axis_bridge | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | Japanese design basis and damage causes | Japanese ground-mount design uses 50-yr snow at allowable stress; most 2014 damage stemmed from inadequate design. | Damage counts or event/design ratios. | adopt | reviewed
WSS-S020 | NEDO/JPEA, 2019 guideline technical annex B (snow load calculation). | https://www.nedo.go.jp/content/100895023.pdf | 2026-10-12 | pp. B-2 to B-3, Fig. B2; pp. B-7 to B-8 | guideline technical annex | validation_only | snow_gravity_load | T2_public_lab_standard_or_physics | partial | none | Feb 2014 snow load vs 0.6 kN/m2 design load at JMA stations | Feb 2014 ground snow load exceeded the 0.6 kN/m2 design value at Tokyo, Yokohama and Kumagaya; rain-on-snow raised load. | PV damage counts; a specific ratio (figure only, not digitised). | adopt | reviewed
WSS-S021 | NITE news release, snow/ice PV breakage accidents FY2018-2021, 2023-01-26 (corrected 2023-03-08). | https://www.nite.go.jp/data/000143998.pdf | 2026-10-12 | p.2 Secs 1-1, 1-2, Figs 2-5; p.3 | regulator accident database | claims_or_field_calibration | snow_gravity_load | T1_claims_or_field_calibrated | direct | direct | reported breakage accidents and damaged MW | 43 accidents FY2018-21 clustered in heavy-snow years; >30 MW damaged; ~77% involve racking damage. | Rates per plant-year; event/design ratios; transfer to US racking. | adopt | reviewed | Supersedes the pv magazine summary (WSS-S008).
WSS-S022 | NEDO/JPEA, 2019 guideline technical annex D, full-scale rack pressure-chamber tests. | https://www.nedo.go.jp/content/100895023.pdf | 2026-10-12 | pp. D-1 to D-7, Table D5 (positive pressure) | full-scale lab test | curve_fit_shape | snow_gravity_load | T2_public_lab_standard_or_physics | partial | direct | failure pressure / manufacturer design pressure, n=6 commercial racks | Measured failure/design ratios 3.28, 1.35, 0.97, 2.17, 2.91, 1.21 for downward uniform pressure; joint slip and buckling govern. | Treating manufacturer design pressure as the ASCE 7-22 design snow load; transfer to trackers without a bridge. | adopt | reviewed | Verified in original by the cell author (extracted text lines for Table D5).
WSS-S023 | Maeda Y., Ozawa Y. et al. (2019), FEM model for ground-mount PV racks, Trans. JSME 85(871) 18-00397. | https://www.jstage.jst.go.jp/article/transjsme/85/871/85_18-00397/_article/-char/ja | 2026-10-12 | Sec 2.1 p.2; Sec 3 pp.3-4; Table 3 | peer-reviewed full-scale test | curve_fit_shape | snow_gravity_load | T2_public_lab_standard_or_physics | partial | direct | post buckling under uniform sandbag snow load vs 1980 Pa design | A properly designed thin-steel rack buckled at 5038-5278 Pa (2.54-2.67 x design) followed by sudden global collapse. | Generalising n=1; non-uniform snow capacity. | adopt | reviewed | Verified in original by the cell author.
WSS-S024 | Maeda Y. et al. (2020), shell-element FEM of the same tests, Mechanical Engineering Journal 7(1) 19-00186. | https://www.jstage.jst.go.jp/article/mej/7/1/7_19-00186/_article/-char/en | 2026-10-12 | abstract; Sec.2; Table 2 | peer-reviewed FEM | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | partial | direct | buckling load prediction | Joint eccentricity omission overstates buckling capacity (design-error mechanism). | Field fragility. | adopt | reviewed
WSS-S025 | Vector Structural Engineering for SunModo, ground mount package A16 calc, ASCE 7-22 (2024). | https://knowledgebase.sunmodo.com/wp-content/uploads/2024/05/FL-GM-Package-A16-calc-ASCE-7-22-Exposure-C-140-mph-70-psf-35-deg.pdf | 2026-10-12 | pp.1, 7-8 | practitioner design calculation | axis_bridge | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | direct | partial | how ASCE 7-22 is applied to ground-mount PV | Ground-mount PV is often Risk Category I, Ce 0.9, Ct 1.2; slippery-surface Cs credit is dropped for low leading edges. | Treating the calc as ASCE text; generalising Risk Category I to all plants. | adopt | reviewed | Printed slope 20 deg vs Cs 0.64 (35 deg) inconsistency recorded.
WSS-S026 | GameChange Solar, Genius Tracker 1P-2R technical datasheet, 2023-01-11 (dead link; search snippet only). | https://gamechangesolar.com/downloads/tracker/GameChange-Solar-Genius_Tracker-1P-2R-Technical_Datasheet-1-11-2023.pdf | 2026-10-12 | snow load row (snippet) | manufacturer specification | selector_archetype | snow_gravity_load | T3_engineering_proxy_or_adjacent_empirical | direct | direct | tracker snow load tiers | Unverified: snow tiers 5/20/40/60 psf. | Citing the tiers as verified. | defer | unavailable | HTTP 404; JL to obtain current datasheet.
WSS-S027 | Ding S., Zhou X., wind-snow combination factor for PV panels, Engineering Mechanics (2025 accepted), abstract. | https://www.engineeringmechanics.cn/article/doi/10.6052/j.issn.1000-4750.2025.03.0090 | 2026-10-12 | abstract | peer-reviewed probabilistic load study | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | partial | wind-snow combination factor | Concurrent wind + snow on trackers is a real design case (factor 0.7, Harbin). | Failure probability. | defer | reviewed | Supports the deferred combined wind-snow pathway.
WSS-S028 | Sato K. (SPEI), 'Case Studies of Accidents and Their Causes in PV Systems', IEA PVPS Task 13 workshop, 2024-11-12. | https://iea-pvps.org/wp-content/uploads/2024/08/05_Kota-Sato_Structural-Damages_PVSEC2024.pdf | 2026-10-12 | slides 3, 11-15, 19 | expert forensic case review | case_study_severity | snow_gravity_load | T1_claims_or_field_calibrated | direct | direct | snow failure-mode taxonomy | Damage ranges from module-only breakage to total loss; eave load, rail joints and pile resistance govern. | Frequencies or load ratios. | adopt | reviewed
WSS-S029 | NEDO, 'Design and construction guideline for ground-mounted PV systems, 2025 edition'. | https://www.nedo.go.jp/content/800023895.pdf | 2026-10-12 | preface; Sec.1; ch.2 Sec 2.2 pp.19-20; Sec 8.4 pp.66-69 | design guideline | mechanism_only | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | eave load and rain-on-snow clauses; damage captions | Older plants designed without eave load and rain-on-snow surcharge form a vulnerable vintage class. | Damage frequencies or load ratios. | adopt | reviewed
WSS-S030 | NITE news release, snow/ice accidents at PV plants FY2020-2024, 2025-11-20. | https://www.nite.go.jp/data/000159577.pdf | 2026-10-12 | p.1; pp.2-3 Figs 1-4; p.4 cases 1-4; p.5 Sec 3 | regulator accident database and inspection findings | claims_or_field_calibration | snow_gravity_load | T1_claims_or_field_calibrated | direct | direct | reported accidents and per-event damaged share of plant | When snow exceeded design, per-event damage was ~37%, ~80% and total collapse; a module-only state exists (~440 kW); one plant designed for 70 cm vs >=160 cm required. | A numeric event/design ratio; rates per plant-year. | adopt | reviewed
WSS-S031 | Jones K., Thorkildson R., Lott N., 'The Development of a U.S. Climatology of Extreme Ice Loads', NOAA/NCDC Technical Report 2002-01, Dec 2002. | https://repository.library.noaa.gov/view/noaa/13832/noaa_13832_DS1.pdf | 2026-10-12 | p.5 Eq.(1) and p.6 (PDF pp.6-7) | government technical report | axis_bridge | snow_gravity_load;ice_accretion | T2_public_lab_standard_or_physics | none | none | Simple model equivalent radial ice thickness | Req = (1/(rho_i pi)) sum[(P rho_o)^2 + (3.6 V W)^2]^0.5 with rho_i = 0.9 g/cm3; with no wind the flat glaze weight equals pi x rho_i x Req x g. | Claiming the no-wind identity is exact when wind contributes (then it overstates flat ice). | adopt | reviewed | Verified in original by the cell author; Simple model underlies the ASCE ice maps.
WSS-S032 | Damage repository value basis, solar_wind_value_breakdown.xlsx (NREL/NLR Q1-2025 UPV PVSCM, 2024 USD). | docs/method/value_basis/solar_wind_value_breakdown.xlsx | 2026-10-12 | Solar_Map rows 2-17; Inputs | repository value workbook | exposure_or_value | snow_gravity_load | T2_public_lab_standard_or_physics | direct | direct | reference $/kWdc value rows | Reference denominators and reconciliation (877.80 physical; 1120 installed). | Implicit site defaults or curve caps. | adopt | reviewed

## Known_Answers
test_id | failure_unit_id | ratio | array_load_kpa | DR_lower | DR_central | DR_upper
structure_direct_ratio_1 | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 1 |  | 0.37034 | 0.20927 | 0.060879
structure_swe150_no_ice_product_tracker | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 1.5323 |  | 0.71258 | 0.53291 | 0.25584
structure_swe120_ice12_fixed | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 1.5724 |  | 0.73073 | 0.55433 | 0.27351
module_swe150_cascade_fixed | WSS1_MODULE_FIELD_BREAKAGE | 1.5323 | 1.1121 | 0.61347 | 0.43322 | 0.2056
module_direct_ratio_and_load | WSS1_MODULE_FIELD_BREAKAGE | 0.8 | 2 | 0.88219 | 0.5738 | 0.25661
structure_tracker_project_rated_5psf | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 1.8581 |  | 0.83252 | 0.68636 | 0.39994
structure_zero_snow | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 0 |  | 0 | 0 | 0
structure_ratio_above_tested_flag | WSS1_SUPPORT_STRUCTURE_COLLAPSE | 3.5 |  | 0.989 | 0.96491 | 0.85776

## QA_Checks
check | status
artifact schema v3 | see validator
value reconciliation 877.80 / 1120 | see validator
known answers independent of evaluator | see validator