## README
field | value
cell_id | winter_storm_wind
model | model v0.1 / docs r1 fail-closed scaffold
runtime | NO_RUNTIME_CURVE: every DR and loss withheld

## Failure_Units
id | subsystem | component | treatment | mechanism_note | value_lineage
WT_BLADE_ASSEMBLY | ROTOR_ASSEMBLY; PITCH_SYSTEM | BLADE; PITCH_DRIVE | candidate_primary_no_curve | ice mass, imbalance and extreme iced-blade loads | Wind_Map rows 2-3
WT_NACELLE_AND_HUB | NACELLE; ROTOR_ASSEMBLY; POWER_ELECTRONICS | HUB; NACELLE_STRUCTURE; GEARBOX; GENERATOR_INTERNAL; YAW_SYSTEM; POWER_CONVERTER | withheld_candidate | ice load transfer; cold effects belong to a separate pathway | Wind_Map rows 4-8
WT_TOWER_AND_EXTERNAL_FIXTURES | TOWER | TOWER_SECTION; ladders; cable trays | withheld_candidate | iced projected area under concurrent wind (deferred pathway) | Wind_Map row 9
WT_PAD_ELECTRICAL | ELECTRICAL_COLLECTION | pad transformers and switchgear | withheld_candidate | ice on enclosures and bushings | Wind_Map row 12 (split required)
WT_COLLECTION_NETWORK | ELECTRICAL_COLLECTION | CABLE_AC (overhead or buried) | withheld_candidate | ice and ice + wind on overhead spans; buried cables not exposed | Wind_Map row 12 (split required)
WT_GSU_SUBSTATION | SUBSTATION | TRANSFORMER_MAIN; SWITCHGEAR; bus | withheld_candidate | ice bridging and bus loads | Wind_Map row 12 (split required)
WT_CONTROL_AND_MET_STATION | SCADA | met masts; control building | withheld_candidate | ice + wind on guyed lattice masts | not in value workbook
WT_FOUNDATION | FOUNDATION | FOUNDATION_BASE | geometry_screened_no_numeric_zero | no direct ice-load pathway; frost heave separate | Wind_Map row 10
WT_CIVIL_INFRA | CIVIL_INFRA | SITE_ACCESS_STAGING_FACILITIES | split_required | building roof snow is a separate asset class | Wind_Map row 11
SUPPORT_FIELDWORK | REPLACEMENT_FIELDWORK | ASSEMBLY_AND_INSTALLATION | allocation_only | allocate once | Wind_Map row 13
SUPPORT_TRANSPORT_LOGISTICS | REPLACEMENT_LOGISTICS | WIND_TURBINE_TRANSPORT | allocation_only | allocate once | Wind_Map row 14

## Legacy_Audit
legacy_unit | L | k | x0_in | DR_at_0_in | DR_at_0.75_in | DR_at_1.5_in | decision
ROTOR_ASSEMBLY | 0.6 | 3.5 | 1.5 | 0.0031321 | 0.040528 | 0.3 | rejected
TOWER | 0.3 | 2 | 2.5 | 0.0020079 | 0.0087937 | 0.035761 | rejected
NACELLE | 0.35 | 3 | 0.75 | 0.033372 | 0.175 | 0.31663 | rejected
ELECTRICAL | 0.7 | 4 | 0.75 | 0.033198 | 0.35 | 0.6668 | rejected

## Value_Crosswalk
value_source_id | source_location | row_or_bucket_id | row_or_bucket_label | value | unit | financial_class | failure_unit_id | applicable_pathway_ids | role_in_loss | include_in_direct_denominator | allocation_rule | double_count_guardrail | status | notes
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!2 | WIND_VALUE_002_BLADE | Blades | 282 | 2023_USD_per_kW | direct_hardware | WT_BLADE_ASSEMBLY | ice_accretion | withheld_direct_value | true | Candidate denominator; ice-load DR withheld. | Do not charge falling-ice damage here. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!3 | WIND_VALUE_003_PITCH | Pitch assembly | 13 | 2023_USD_per_kW | direct_hardware | WT_BLADE_ASSEMBLY | ice_accretion | withheld_direct_value | true | Grouped with the rotor for ice loading; withheld. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!4 | WIND_VALUE_004_HUB | Hub assembly | 42 | 2023_USD_per_kW | direct_hardware | WT_NACELLE_AND_HUB | ice_accretion | withheld_direct_value | true | Withheld. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!5 | WIND_VALUE_005_NACELLE_STRUCTURE | Nacelle structural assembly | 76 | 2023_USD_per_kW | direct_hardware | WT_NACELLE_AND_HUB | ice_accretion | withheld_direct_value | true | Withheld; cold effects are another pathway. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!6 | WIND_VALUE_006_DRIVETRAIN | Drivetrain assembly | 236 | 2023_USD_per_kW | direct_hardware | WT_NACELLE_AND_HUB | ice_accretion | withheld_direct_value | true | Withheld. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!7 | WIND_VALUE_007_POWER_CONVERTER | Nacelle electrical assembly | 137 | 2023_USD_per_kW | direct_hardware | WT_NACELLE_AND_HUB | ice_accretion | withheld_direct_value | true | Withheld. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!8 | WIND_VALUE_008_YAW | Yaw assembly | 28 | 2023_USD_per_kW | direct_hardware | WT_NACELLE_AND_HUB | ice_accretion | withheld_direct_value | true | Withheld. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!9 | WIND_VALUE_009_TOWER | Tower module | 276 | 2023_USD_per_kW | direct_hardware | WT_TOWER_AND_EXTERNAL_FIXTURES | ice_accretion | withheld_direct_value | true | Withheld (ice + wind deferred). | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!10 | WIND_VALUE_010_FOUNDATION | Foundation | 120 | 2023_USD_per_kW | direct_hardware | WT_FOUNDATION | ice_accretion | withheld_direct_value | true | Withheld; frost heave is another pathway. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!11 | WIND_VALUE_011_CIVIL | Site access, staging, and facilities | 47 | 2023_USD_per_kW | civil | WT_CIVIL_INFRA | ice_accretion | split_required | true | Mixed subjects; buildings snow load deferred. | None charged. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!12 | WIND_VALUE_012_ELECTRICAL | Electrical infrastructure (collection + substation) | 72 | 2023_USD_per_kW | mixed | WT_PAD_ELECTRICAL;WT_COLLECTION_NETWORK;WT_GSU_SUBSTATION | ice_accretion | split_required | true | Split overhead collection, buried collection and substation before any line curve. | Never apply a line DR to the merged row. | withheld
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!13 | WIND_VALUE_013_ASSEMBLY | Assembly and installation | 100 | 2023_USD_per_kW | support_logistics | SUPPORT_FIELDWORK | ice_accretion | support_once | false | Allocate once after qualified damage. | No independent DR. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!14 | WIND_VALUE_014_TRANSPORT | Wind turbine transport | 194 | 2023_USD_per_kW | support_logistics | SUPPORT_TRANSPORT_LOGISTICS | ice_accretion | support_once | false | Allocate once after qualified damage. | No independent DR. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!15 | WIND_VALUE_015_ENGINEERING | Engineering and development | 36 | 2023_USD_per_kW | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | ice_accretion | excluded | false | Excluded. | Never in the physical denominator. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!16 | WIND_VALUE_016_PROJECT_MANAGEMENT | Project management | 14 | 2023_USD_per_kW | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | ice_accretion | excluded | false | Excluded. | Never in the physical denominator. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!17 | WIND_VALUE_017_CONSTRUCTION_FINANCE | Construction finance | 111 | 2023_USD_per_kW | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | ice_accretion | excluded | false | Excluded. | Never in the physical denominator. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!18 | WIND_VALUE_018_CONTINGENCY | Contingency | 54 | 2023_USD_per_kW | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | ice_accretion | excluded | false | Excluded. | Never in the physical denominator. | mapped
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!19 | WIND_VALUE_019_WARRANTY | Wind turbine warranty | 130 | 2023_USD_per_kW | excluded_soft_sunk | OUTSIDE_PHYSICAL_CELL | ice_accretion | excluded | false | Excluded. | Never in the physical denominator. | mapped

## Parameter_Tiers
parameter | pathway_id | curve_id | value | param_role | tier | source_ids | reasoning | status | update_trigger
runtime_curve_count | ice_accretion | none | 0 | capability | T4_placeholder_or_expert_judgment | WSW-S017 | No curve passed the evidence chain. | adopt | Reviewed output-bearing release.
canonical_runtime_artifact | ice_accretion | none | false | release_state | T4_placeholder_or_expert_judgment | WSW-S017 | Repository scaffold only. | adopt | Explicit promotion.
pathway_id | ice_accretion | none | ice_accretion; no default | pathway_identity | T4_placeholder_or_expert_judgment | WSW-S007 | Separate winter mechanisms. | adopt | Governed pathway redesign.
event_family_id_required | ice_accretion | none | true | compound_event_control | T4_placeholder_or_expert_judgment | WSW-S002 | One parent winter storm binds snow, ice, cold and flood children. | adopt | Consumer contract change.
ice_radial_thickness_field | ice_accretion | none | ice_radial_thickness_mm | axis_source_field | T2_public_lab_standard_or_physics | WSW-S011;WSW-S020 | Standard ice intensity. | capture_only | ASCE 7-22 text.
ice_concurrent_gust_field | ice_accretion | none | ice_concurrent_gust_3s_10m_mps | axis_source_field | T2_public_lab_standard_or_physics | WSW-S011 | Ice + wind design case. | capture_only | ASCE 7-22 text.
design_ice_thickness_field | ice_accretion | none | design_ice_thickness_mm | axis_source_field | T2_public_lab_standard_or_physics | WSW-S011 | Needed for overhead-line event/design ratio. | capture_only | Line design records.
legacy_curve_reuse | ice_accretion | none | rejected | legacy_control | T4_placeholder_or_expert_judgment | WSW-S019;WSW-S001 | Fails zero-input and case checks. | reject | None.
overhead_line_candidate_median | ice_accretion | none | ~3 x design ice (documented, inactive) | open_seam_placeholder | T3_engineering_proxy_or_adjacent_empirical | WSW-S014;WSW-S013 | Field withstand anchor. | defer | Li et al. 2024; topology; value split.

## Claim_Register
claim_id | pathway_id | claim_text | claim_type | source_ids | exact_locator | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
WSW-C001 | ice_accretion | Winter storm on a wind farm is several mechanisms; ice accretion is the v0.1 primary candidate. | governance_decision | WSW-S007;WSW-S002 | RP13 pp.12-31; NERC p.76 | T4_placeholder_or_expert_judgment | pathway_id=ice_accretion primary candidate; deferred: ice_with_concurrent_wind, ice_shedding_impact, snow_gravity_load_buildings | adopt | Govern ice accretion separately from shedding, ice+wind and snow on buildings. | Defaulting winter mechanisms together. | JL checkpoint-1 decision; standard 18 split. | Governed pathway redesign.
WSW-C002 | ice_accretion | The legacy winter x wind curves fail zero-input and case-study checks. | direct_observation | WSW-S019 | Secs 6.1-6.2 | T4_placeholder_or_expert_judgment | legacy curves | reject | Record rejection. | Reuse of any legacy curve. | Logistic curves are not zero at zero ice (nacelle and electrical ~3.3%); predict 17-35% DR at 0.75 in where the cited event shows none; ignore site design. | None; replacement needs new evidence.
WSW-C003 | ice_accretion | PNNL-33587 does not support the legacy ice fragility numbers. | direct_observation | WSW-S001;WSW-S019 | PNNL Sec 3.7, 5.1; legacy Secs 1.6, 4.3 | T3_engineering_proxy_or_adjacent_empirical | legacy citation audit | reject | Record that the cited fragility figures do not say what the legacy note claims. | Citing PNNL as turbine ice fragility. | 15/30/45 mm curves are telecom towers on wind speed; Fig.35 is a tension tower near zero below ~60 mm. | Primary papers.
WSW-C004 | ice_accretion | In February 2021, blade icing caused 48 outages or derates at 41 wind facilities; no physical damage was reported. | direct_observation | WSW-S002;WSW-S003 | NERC p.76; FERC slide 12 | T1_claims_or_field_calibrated | boundary evidence | adopt | Treat Feb 2021 as a large icing event with availability losses and no reported physical damage. | Proven zero damage. | Official report describes protective shutdowns and derates only. | Insurer claims data.
WSW-C005 | ice_accretion | No located evidence quantifies physical damage to turbines from ice accretion load. | direct_observation | WSW-S017;WSW-S007;WSW-S012 | search log; RP13 | T4_placeholder_or_expert_judgment | WT turbine equipment under ice_accretion: withheld (NO_RUNTIME_CURVE) | withhold | Withhold numeric output; not available because evidence is lacking. | Declaring DR approximately zero. | No turbine structural ice failure located; absence of reports is bounded evidence, not proof (JL checkpoint-2 decision). | Field/claims/work-order evidence of ice-load damage or its absence at known ice thickness.
WSW-C006 | ice_accretion | Overhead lines designed for 13 mm of ice withstood about 30-50 mm in 1998. | source_interpretation | WSW-S013;WSW-S014;WSW-S009 | H-Q pages; INMR; record | T3_engineering_proxy_or_adjacent_empirical | overhead collection line candidate: median ~3 x design ice, documented only | defer | Document the first candidate anchor; no runtime curve in v0.1. | Activating it without topology and value split. | Field withstand of 13-mm-design lines was 30-50 mm; value row merges collection and substation; reference farm assumes buried collection. | Li et al. 2024 coefficients; site overhead share; split value row.
WSW-C007 | ice_accretion | Met masts not designed for site ice can collapse. | source_interpretation | WSW-S007;WSW-S018 | RP13 p.18; snippet | T3_engineering_proxy_or_adjacent_empirical | met mast: withheld | withhold | Record met masts as the most ice-fragile wind-farm structure; no curve. | A met-mast DR. | Qualitative collapse evidence only. | Met-mast ice failure data.
WSW-C008 | ice_accretion | The one located wind-farm ice damage case was caused mostly by falling ice. | direct_observation | WSW-S015 | article body | T4_placeholder_or_expert_judgment | ice_shedding_impact: deferred pathway | defer | Route falling-ice damage to the deferred shedding pathway. | Charging shedding damage to accretion load. | Blue Canyon 2010 damage came mostly from falling ice during thaw. | Shedding-specific evidence.
WSW-C009 | ice_accretion | Radial ice thickness at 10 m with concurrent gust is the standard ice-load intensity. | source_interpretation | WSW-S011;WSW-S020 | Ch.10 (secondary); Eq.(1) | T2_public_lab_standard_or_physics | axis: ice_radial_thickness_mm (equivalent uniform radial glaze at 10 m, 25.4 mm cylinder) + ice_concurrent_gust_3s_10m_mps | adopt | Declare the future axis and required capture fields. | Treating design ice as a failure threshold. | Matches ASCE 7 Ch.10 and the Simple model. | ASCE 7-22 Ch.10 text (JL).
WSW-C010 | ice_accretion | Icing downtime and cold shutdowns are business interruption, not physical damage. | governance_decision | WSW-S002;WSW-S007 | NERC pp.169-170; RP13 | T4_placeholder_or_expert_judgment | excluded: curtailment, icing downtime, freeze-off, cold limits | adopt | Keep business interruption outside the damage curve. | Folding downtime into DR. | Physical destruction only (repo scope). | None.

## Source_Register
source_id | citation | url | accessed_on | exact_locator | source_type | source_role | pathway_ids | evidence_tier | target_asset_match | target_failure_unit_match | measured_or_modeled_endpoint | permitted_inference | prohibited_inference | decision | status | notes
WSW-S001 | Kabre W., Weimar M.R., 'Fragility Functions Resource Report', PNNL-33587, Oct 2022. | https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-33587.pdf | 2026-10-12 | Tables 1.1-1.2; Sec 3.7 Fig.16 (report p.23); Sec 5.1 Fig.35 (report p.43) | national-lab compendium | rejected | ice_accretion | T3_engineering_proxy_or_adjacent_empirical | none | adjacent | telecom tower vs top wind speed with ice; tension tower vs ice thickness (no wind) | Order-of-magnitude: lattice tension tower failure onset ~60 mm, median ~70 mm radial ice (no wind). | Any turbine fragility; any damage ratio; Fig.16 as an ice-thickness fragility. | demote | reviewed | Legacy note misattributes and misreads these figures.
WSW-S002 | FERC-NERC-Regional Entity Joint Staff, 'The February 2021 Cold Weather Outages in Texas and the South Central United States', Nov 2021. | https://www.nerc.com/pa/rrm/ea/Documents/February_2021_Cold_Weather_Report.pdf | 2026-10-12 | p.76 (PDF p.77) Sec 'Wind Turbine Generator Freezing Issues'; pp.169-170 (PDF pp.170-171) 'Blade Icing' | official investigation | validation_only | ice_accretion | T1_claims_or_field_calibrated | direct | direct | outages, derates, failures to start | Blade icing caused '48 outages or derates at 41 wind facilities' (SPP, Feb 8-9); shutdowns 'to prevent equipment damage'; no physical damage reported. | Inferring zero damage as proven; any damage ratio. | adopt | reviewed | Downloaded from NERC and read by the cell author.
WSW-S003 | FERC staff presentation of the final report, 'FERC Presentation-Phase 2', Nov 2021. | https://www.nerc.com/pa/Stand/Project202107ExtremeColdWeatherDL/FERC%20Presentation-Phase%202.pdf | 2026-10-12 | slides 7, 11, 12, 17 | official staff summary | validation_only | ice_accretion | T1_claims_or_field_calibrated | direct | direct | freeze-related outage shares | Blade icing was 32% of freeze-related outages in ERCOT and SPP (availability endpoint). | Damage inference. | adopt | reviewed
WSW-S004 | FERC staff open-meeting presentation, preliminary findings, Sep 2021. | https://www.ferc.gov/sites/default/files/2021-09/2021%20Cold%20Weather%20Inquiry%20Open%20Meeting%20Presentation%20_PPT%20Version.pdf | 2026-10-12 | slide 8 | official staff summary | validation_only | ice_accretion | T2_public_lab_standard_or_physics | direct | direct | outage causes | Frozen instrumentation and blade icing were the largest freeze sub-causes. | Damage inference. | adopt | reviewed
WSW-S005 | Rezaei S.N., Chouinard L., Legeron F., Langlois S., 'Vulnerability Analysis of Transmission Towers subjected to Unbalanced Ice Loads', ICASP12, 2015. | https://open.library.ubc.ca/cIRcle/collections/53032/items/1.0076203 | 2026-10-12 | known via PNNL Fig.35 only | conference paper | rejected | ice_accretion | T2_public_lab_standard_or_physics | none | adjacent | tension tower failure vs ice thickness | Not read; known only through PNNL. | Any parameter until read. | defer | unavailable | UBC block page; JL to download.
WSW-S006 | ArcVera Renewables, 'ERCOT Market Cold Weather Failure 10-19 February 2021' (press release reprint). | https://www.nacleanenergy.com/wind/new-study-by-leading-renewables-consultant-arcvera-shows-texas-icing-event-led-to-over-4-billion-financial-loss-for-wind-farms | 2026-10-12 | press release | consultant press release (secondary) | validation_only | ice_accretion | T4_placeholder_or_expert_judgment | direct | none | lost production valued at market prices | Feb 2021 wind losses were lost production ($4.18B gross transfer), not repair cost. | Treating $4.18B as damage. | adopt | reviewed | Publisher DNS failure; report not read.
WSW-S007 | IEA Wind TCP Task 19, Recommended Practice 13, 'Wind Energy Projects in Cold Climates', 2nd ed. 2017. | https://iea-wind.org/wp-content/uploads/2022/12/RP-13.2-Cold-Climates.pdf | 2026-10-12 | pp.12, 15, 17 Table 3-1, 18, 29, 31 | international recommended practice | mechanism_only | ice_accretion | T2_public_lab_standard_or_physics | direct | partial | icing duration and production loss classes | Icing is primarily a production-loss peril; met masts not designed for ice can collapse; overhead cables can be damaged. | A thickness-based damage ratio; ice class as radial-ice intensity. | adopt | reviewed
WSW-S008 | Liu, Wang, Liu (2026), extreme ice accretion damage on electricity infrastructure in China, IJDRS 17(3):548-570. | https://journal.hep.com.cn/ijodrs/EN/10.1007/s13753-026-00730-0 | 2026-10-12 | abstract | peer-reviewed paper | mechanism_only | ice_accretion | T2_public_lab_standard_or_physics | none | adjacent | HV line/tower failure drivers | Ice load dominates HV line failures in freezing rain. | Turbine damage; thickness medians (not read). | adopt | reviewed
WSW-S009 | Li, Darestani, Dai, Ma (2024), parametrized fragility of distribution systems under ice and concurrent wind, Structure and Infrastructure Engineering. | https://digitalcommons.mtu.edu/michigantech-p2/1231 | 2026-10-12 | record only | peer-reviewed paper | curve_form | ice_accretion;ice_with_concurrent_wind | T2_public_lab_standard_or_physics | none | adjacent | distribution pole/conductor fragility under ice + wind | Closest analogue for overhead 34.5 kV collection lines. | Any coefficient until read. | defer | unavailable | Paywalled; JL to obtain.
WSW-S011 | ASCE/SEI 7-22 Chapter 10, Ice Loads - Atmospheric Icing (secondary descriptions). | https://amplify.asce.org/content/standard/9780784415788/part/provisions/standard-chapter/s10 | 2026-10-12 | Ch.10 (not read) | consensus standard | axis_bridge | ice_accretion | T2_public_lab_standard_or_physics | partial | partial | nominal radial ice at 33 ft with concurrent gust | Intensity definition: equivalent radial glaze ice at 10 m with concurrent 3-s gust (to verify). | Design value as a failure threshold; edition-specific clauses unverified. | defer | unavailable | Paywalled; legacy importance-factor statements look like ASCE 7-16.
WSW-S012 | IEC 61400-1:2019 (Ed.4) and AMD1:2025, Design requirements (abstract only). | https://webstore.iec.ch/en/publication/111042 | 2026-10-12 | abstract | consensus standard | mechanism_only | ice_accretion | T1_claims_or_field_calibrated | direct | partial | turbine design requirements | Turbines are designed to a turbine class, not local ice maps. | Legacy Annex L table/clause numbers and partial factors (unverified). | defer | unavailable
WSW-S013 | Hydro-Quebec, 'Ice storm 1998' pages (A perfect storm; After the storm). | https://www.hydroquebec.com/ice-storm-1998/a-perfect-storm.html | 2026-10-12 | page body | utility first-party account | case_study_severity | ice_accretion | T2_public_lab_standard_or_physics | adjacent | adjacent | transmission failures vs ice | Lines designed for ~45 mm failed when ice reached roughly 50-100 mm. | Per-tower fragility; wind-farm inference. | adopt | reviewed
WSW-S014 | INMR, 'Looking Back on the Great Ice Storm of 1998', 2020 (updated 2025). | https://www.inmr.com/?p=8270 | 2026-10-12 | article body | trade magazine | case_study_severity | ice_accretion | T3_engineering_proxy_or_adjacent_empirical | adjacent | adjacent | line withstand vs design ice | Lines designed for 13 mm withstood about 30-50 mm; massive pole failures at 40-100 mm. | Precise fragility medians. | adopt | reviewed | First candidate anchor for overhead collection lines (documented, not activated).
WSW-S015 | KSWO, 'Blue Canyon Wind Farm still recovering from Winter Wallop', Feb 2010. | https://www.kswo.com/story/12032582/blue-canyon-wind-farm-still-recovering-from-winter-wallop | 2026-10-12 | article body | local news | case_study_severity | ice_shedding_impact | T4_placeholder_or_expert_judgment | direct | partial | repair cost after ice storm | About $1M of damage across 195 turbines, mostly from falling ice during thaw. | Any curve; attributing cost to ice-load accretion. | adopt | reviewed | Context for the deferred ice-shedding pathway.
WSW-S016 | S&P Global Market Intelligence, 'Renewables insurer unfazed by Texas freeze', Mar 2021 (snippet only). | https://www.spglobal.com/market-intelligence/en/news-insights/articles/2021/3/renewables-insurer-unfazed-by-texas-freeze-but-extreme-weather-risks-set-to-rise-63036095 | 2026-10-12 | article (HTTP 403) | trade press | validation_only | ice_accretion | T3_engineering_proxy_or_adjacent_empirical | direct | none | claims count | Unverified: 'three claims' related to the freeze. | Claim severity; zero-damage assertion. | defer | unavailable
WSW-S017 | Bounded search record: no cost-based icing damage function for wind turbines located. | BOUNDED_SEARCH_LOG | 2026-10-12 | search log Sec 3 | search record | validation_only | ice_accretion | T4_placeholder_or_expert_judgment | direct | direct | absence within search scope | No thickness-to-damage-ratio function and no modern turbine structural ice failure located within the logged search. | Universal nonexistence. | adopt | reviewed
WSW-S018 | Mulherin N.D., 'Atmospheric icing and communication tower failure in the United States', Cold Regions Sci. Tech., 1998 (snippet). | https://doi.org/10.1016/S0165-232X(98)00002-8 | 2026-10-12 | snippet only | peer-reviewed paper | mechanism_only | ice_accretion | T3_engineering_proxy_or_adjacent_empirical | adjacent | adjacent | communication tower ice failures | Ice + wind collapses of lattice/guyed masts are documented. | Counts specific to wind met masts. | defer | unavailable
WSW-S019 | Legacy research note WINTER_WEATHER_x_WIND.md, infrasure-damage-curves @12653b2c (Mar 2026). | https://github.com/Divi-patel/infrasure-damage-curves/blob/12653b2c3d5a013c9524228243ea666c35bb3814/research/WINTER_WEATHER_x_WIND.md | 2026-10-12 | Secs 1.7, 2.5, 3.4, 4.5, 5, 6.1-6.2 | legacy research note | rejected | ice_accretion | T4_placeholder_or_expert_judgment | direct | direct | proposed logistic curves on radial ice thickness | Mechanism inventory and channel split (physical vs curtailment) only. | Any of the four logistic curves or their parameters. | reject | reviewed | Rejected: nonzero DR at zero ice; contradicts own Texas-2021 case; misread PNNL; ignores design.
WSW-S020 | Jones K., Thorkildson R., Lott N., NOAA/NCDC Technical Report 2002-01, Dec 2002. | https://repository.library.noaa.gov/view/noaa/13832/noaa_13832_DS1.pdf | 2026-10-12 | p.5 Eq.(1); p.6 | government technical report | axis_bridge | ice_accretion | T2_public_lab_standard_or_physics | none | none | Simple-model equivalent radial ice thickness | The radial ice axis is the Simple-model equivalent uniform radial thickness, independent of wire diameter. | Treating it as blade ice mass. | adopt | reviewed
WSW-S021 | Damage repository value basis, solar_wind_value_breakdown.xlsx (NREL CWER 2024, 2023 USD). | docs/method/value_basis/solar_wind_value_breakdown.xlsx | 2026-10-12 | Wind_Map rows 2-19 | repository value workbook | exposure_or_value | ice_accretion | T2_public_lab_standard_or_physics | direct | direct | reference $/kW value rows | Reference denominators (1623 physical; 1968 installed). | Implicit site defaults. | adopt | reviewed

## QA_Checks
check | status
curve_records empty | see validator
all metrics withheld | see validator