## README
TC wind x solar | model v2.1 | docs r1
Purpose | coverage-complete screening physical DR and scenario loss
Canonical | FALSE
Curve records | 10
Physical value coverage | 1

## Curve_Records
curve_id | pathway_id | failure_unit_id | curve_form | x_axis | y_axis | parameters | valid_range | interpolation_policy | extrapolation_policy | selector_match | source_parameter_refs | metadata_flags
TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | tropical_cyclone_wind | PV_PERRY_GROUND_FIXED_VISIBLE_MODULE_HARDWARE_SOURCE_UNIT | piecewise_linear | perry_event_max_gust_mps | failure_unit_damage_ratio | {"points": [[17.4, 0.0], [18.3, 0.0], [20.7, 0.00027276656], [24.6, 0.00027276656], [24.8, 0.000955175835], [25.1, 0.000955175835], [25.9, 0.001853190692857], [29.5, 0.001853190692857], [29.8, 0.004054775905], [31.7, 0.00441454805], [37.9, 0.00441454805], [38.9, 0.0182729376325], [39.1, 0.0182729376325]]} | [17.4, 39.1] | linear_between_source_knots | withhold outside 17.4 through 39.1 m/s; no endpoint clamp and no use of the 48.2 m/s audit-only observation | {"array_architecture_id": "PERRY_GROUND_NONTRACKING_SOURCE_COHORT_V1", "causal_scope_acknowledgement_id": "SOURCE_COMPOSITE_HURRICANE_MODULE_LOSS", "module_value_distribution_assumption_id": "UNIFORM_MODULE_HARDWARE_VALUE", "source_population_match_id": "PERRY_MANUAL_GROUND_NONTRACKING_MIXED_SCALE_V1", "source_wind_product_id": "PERRY_DATASET_REPORTED_EVENT_MAX_GUST", "visible_damage_disposition_assumption_id": "FULL_REPLACEMENT_IF_VISIBLE_OR_MISSING"} | ["TCWS-S020#manual_csv_ground_tracking_false_x_le_39_1", "TCWS-S021#manual_endpoint_definition", "FIT_SUFFICIENT_STATISTICS_tropical_cyclone_wind_solar__model_v1_0__docs_r1.csv"] | ["SCREENING_REMOTE_SENSING_LABELED_VISIBLE_FRACTION_WITH_T4_ECONOMIC_BRIDGE", "SOURCE_COHORT_MIXED_SCALE", "SOURCE_COMPOSITE_HURRICANE_MODULE_LOSS", "VISIBLE_DAMAGE_ONLY_HIDDEN_DAMAGE_UNOBSERVED", "SPARSE_SEVERE_TAIL_WITHHELD", "EVENT_CLUSTERED_SAMPLE", "PAVA_DERIVED_KNOTS", "EQUAL_SITE_WEIGHT_NOT_MODULE_WEIGHTED", "CROSS_METHOD_SAME_EVENT_ENDPOINT_CONFLICT", "NO_EXTRAPOLATION", "CURVE_INTRINSIC_SPREAD_NOT_CARRIED"]
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | tropical_cyclone_wind | PV_FIXED_TILT_MODULE_FIELD | ordered_damage_state_lognormal | architecture_specific_tropical_cyclone_wind_demand_index | failure_unit_damage_ratio | {"beta_ln": 0.3, "capacity_scenarios": [{"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.65, 1.2], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.85, 1.55], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.05, 1.95], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "no direct physical module-field repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["modules", "frames", "clamps"], "cost_ratio": 0.1, "description": "localized module, frame, or retention replacement; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS1_LOCALIZED_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["module field"], "cost_ratio": 1.0, "description": "replace the exposed module-field failure unit; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS2_FIELD_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | tropical_cyclone_wind | PV_FIXED_TILT_SUPPORT_STRUCTURE | ordered_damage_state_lognormal | architecture_specific_tropical_cyclone_wind_demand_index | failure_unit_damage_ratio | {"beta_ln": 0.3, "capacity_scenarios": [{"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.9, 1.2, 1.5], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.15, 1.55, 1.9], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.45, 1.95, 2.35], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "no direct structural repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["rails", "braces", "connections"], "cost_ratio": 0.15, "description": "localized connection, rail, brace, or post repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["exposed fixed-tilt support structure"], "cost_ratio": 1.0, "description": "full replacement of the support/SBOS failure unit; module disposition is outside this unit and excluded pending a governed joint-state model; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS2_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["exposed fixed-tilt support structure"], "cost_ratio": 1.0, "description": "terminal destructive failure of the support/SBOS failure unit only; module disposition and any cascade are excluded pending a governed joint-state model; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS3_TERMINAL_UNIT_FAILURE", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | tropical_cyclone_wind | PV_TRACKER_MODULE_FIELD | ordered_damage_state_lognormal | architecture_specific_tropical_cyclone_wind_demand_index | failure_unit_damage_ratio | {"beta_ln": 0.275, "capacity_scenarios": [{"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.8, 1.15], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.95, 1.4], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.1, 1.7], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "no direct physical module-field repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["modules", "frames", "clamps"], "cost_ratio": 0.1, "description": "localized module, frame, or retention replacement; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS1_LOCALIZED_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["module field"], "cost_ratio": 1.0, "description": "replace the exposed tracker module-field failure unit; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "MODULE_DS2_FIELD_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | tropical_cyclone_wind | PV_TRACKER_SBOS_ASSEMBLY | ordered_damage_state_lognormal | architecture_specific_tropical_cyclone_wind_demand_index | failure_unit_damage_ratio | {"beta_ln": 0.275, "capacity_scenarios": [{"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.95, 1.15, 1.35], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.15, 1.4, 1.65], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted synthetic normalized-demand response scenario; not fitted, not a percentile, and not a hazard-specific calibration", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.35, 1.7, 2.0], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "no direct tracker structural repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["torque tube", "bearings", "drive", "connections"], "cost_ratio": 0.15, "description": "localized tracker structural or drive-row repair; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["exposed tracker structural-BOS assembly"], "cost_ratio": 1.0, "description": "full replacement of the support/SBOS failure unit; module disposition is outside this unit and excluded pending a governed joint-state model; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS2_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["exposed tracker structural-BOS assembly"], "cost_ratio": 1.0, "description": "terminal destructive failure of the support/SBOS failure unit only; module disposition and any cascade are excluded pending a governed joint-state model; synthetic coverage state cost, not an observed or calibrated hazard consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "STRUCT_DS3_TERMINAL_UNIT_FAILURE", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | tropical_cyclone_wind | PV_FOUNDATION | ordered_damage_state_lognormal | site_facility_tropical_cyclone_wind_demand_ratio | failure_unit_damage_ratio | {"beta_ln": 0.35, "capacity_scenarios": [{"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.84, 1.12, 1.44], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.05, 1.4, 1.8], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.3125, 1.75, 2.25], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "foundation and anchorage unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "FOUNDATION_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["foundation and anchorage unit"], "cost_ratio": 0.05, "description": "foundation and anchorage unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "FOUNDATION_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["foundation and anchorage unit"], "cost_ratio": 0.35, "description": "foundation and anchorage unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "FOUNDATION_DS2_MAJOR_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["foundation and anchorage unit"], "cost_ratio": 1.0, "description": "foundation and anchorage unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "FOUNDATION_DS3_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | tropical_cyclone_wind | PV_POWER_CONVERSION_AND_COLLECTION | ordered_damage_state_lognormal | site_facility_tropical_cyclone_wind_demand_ratio | failure_unit_damage_ratio | {"beta_ln": 0.35, "capacity_scenarios": [{"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.72, 1.0, 1.32], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.9, 1.25, 1.65], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.125, 1.5625, 2.0625], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "power-conversion and collection unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "POWER_COLLECTION_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["power-conversion and collection unit"], "cost_ratio": 0.1, "description": "power-conversion and collection unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "POWER_COLLECTION_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["power-conversion and collection unit"], "cost_ratio": 0.4, "description": "power-conversion and collection unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "POWER_COLLECTION_DS2_MAJOR_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["power-conversion and collection unit"], "cost_ratio": 1.0, "description": "power-conversion and collection unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "POWER_COLLECTION_DS3_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | tropical_cyclone_wind | PV_GSU_SUBSTATION | ordered_damage_state_lognormal | site_facility_tropical_cyclone_wind_demand_ratio | failure_unit_damage_ratio | {"beta_ln": 0.35, "capacity_scenarios": [{"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.76, 1.04, 1.36], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.95, 1.3, 1.7], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.1875, 1.625, 2.125], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "GSU and substation yard unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "GSU_SUBSTATION_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["GSU and substation yard unit"], "cost_ratio": 0.08, "description": "GSU and substation yard unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "GSU_SUBSTATION_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["GSU and substation yard unit"], "cost_ratio": 0.35, "description": "GSU and substation yard unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "GSU_SUBSTATION_DS2_MAJOR_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["GSU and substation yard unit"], "cost_ratio": 1.0, "description": "GSU and substation yard unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "GSU_SUBSTATION_DS3_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | tropical_cyclone_wind | PV_SCADA_COMMUNICATIONS | ordered_damage_state_lognormal | site_facility_tropical_cyclone_wind_demand_ratio | failure_unit_damage_ratio | {"beta_ln": 0.35, "capacity_scenarios": [{"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.6, 0.84, 1.16], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.75, 1.05, 1.45], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.9375, 1.3125, 1.8125], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "SCADA, communications, controls, and sensor unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "SCADA_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["SCADA, communications, controls, and sensor unit"], "cost_ratio": 0.15, "description": "SCADA, communications, controls, and sensor unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "SCADA_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["SCADA, communications, controls, and sensor unit"], "cost_ratio": 0.55, "description": "SCADA, communications, controls, and sensor unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "SCADA_DS2_MAJOR_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["SCADA, communications, controls, and sensor unit"], "cost_ratio": 1.0, "description": "SCADA, communications, controls, and sensor unit screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "SCADA_DS3_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | tropical_cyclone_wind | PV_CIVIL_INFRA | ordered_damage_state_lognormal | site_facility_tropical_cyclone_wind_demand_ratio | failure_unit_damage_ratio | {"beta_ln": 0.35, "capacity_scenarios": [{"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "lower_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.64, 0.92, 1.28], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "central_screening", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [0.8, 1.15, 1.6], "tier": "T4_placeholder_or_expert_judgment"}, {"interpretation": "unweighted screening resistance scenario on a qualified site-facility demand/design ratio; not fitted and not a probabilistic confidence bound", "scenario_id": "upper_resistance", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_medians": [1.0, 1.4375, 2.0], "tier": "T4_placeholder_or_expert_judgment"}], "damage_states": [{"affected_subsystems": [], "cost_ratio": 0.0, "description": "wind-exposed civil infrastructure bucket screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "CIVIL_DS0_NO_DIRECT_DAMAGE", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["wind-exposed civil infrastructure bucket"], "cost_ratio": 0.08, "description": "wind-exposed civil infrastructure bucket screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "CIVIL_DS1_LOCALIZED_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["wind-exposed civil infrastructure bucket"], "cost_ratio": 0.35, "description": "wind-exposed civil infrastructure bucket screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "CIVIL_DS2_MAJOR_REPAIR", "tier": "T4_placeholder_or_expert_judgment"}, {"affected_subsystems": ["wind-exposed civil infrastructure bucket"], "cost_ratio": 1.0, "description": "wind-exposed civil infrastructure bucket screening disposition; explicit Tier-4 coverage assumption, not an observed or calibrated TC-wind consequence", "source_ids": ["TCWS2_CELL_LOCAL_SYNTHETIC_DECISION", "NO_DIRECT_TC_CALIBRATION_SOURCE"], "state_id": "CIVIL_DS3_FULL_UNIT_REPLACEMENT", "tier": "T4_placeholder_or_expert_judgment"}]}

## Value_Crosswalk
value_source_id | source_location | row_or_bucket_id | row_or_bucket_label | value | unit | financial_class | failure_unit_id | applicable_pathway_ids | role_in_loss | include_in_direct_denominator | allocation_rule | double_count_guardrail | status | notes
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!2 | SOLAR_VALUE_002_MODULE | Module hardware + manufacturing allocation | 291.21485143992487 | 2024_USD_per_kWdc | direct_hardware | PV_FIXED_TILT_MODULE_FIELD¦PV_TRACKER_MODULE_FIELD | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Never charge both architectures, reuse a neighboring-pathway DR, or charge module replacement again through a future terminal-structure rule. | included_v2_1_screening_reference | Exact Q1-2025 reference row reused from strong_wind_solar; TCWS-S013 is the cell source-register cross-reference. Benchmark is not an implicit site default or cap.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!3 | SOLAR_VALUE_003_MOUNTING | Tracker/racking hardware | 109.98972602739727 | 2024_USD_per_kWdc | direct_hardware | PV_FIXED_TILT_SUPPORT_STRUCTURE¦PV_TRACKER_SBOS_ASSEMBLY | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not split torque tube, drive, rails, piles, and foundations beyond source support; do not sum fixed and tracker units or inherit strong-wind curves. | included_v2_1_screening_reference | Architecture-generic reference row; v2 synthetic DR records exist, but this benchmark is not a runtime value binding or composition proof.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!4 | SOLAR_VALUE_004_FOUNDATION | Driven piers + inverter pad | 31.12448715327472 | 2024_USD_per_kWdc | direct_hardware | PV_FOUNDATION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Never inherit module/support DR or include surge, flood, or scour in this pathway. | included_v2_1_screening_reference | Mixed foundation bucket; absence of a curve is not zero damage.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!5 | SOLAR_VALUE_005_INVERTER | Central inverter hardware | 32.306366410372384 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_COLLECTION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not apply array pressure DR or array exposed fraction. | included_v2_1_screening_reference | No qualified direct TC-wind inverter curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!6 | SOLAR_VALUE_006_COMBINER | Combiner boxes | 6.82625 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_COLLECTION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not pool with inverter, cable, GSU, or module response; debris and ingress are excluded pathways. | included_v2_1_screening_reference | No qualified direct aerodynamic curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!7 | SOLAR_VALUE_007_CABLE | AC and DC conductors and project electrical line | 69.3201119402985 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_COLLECTION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not reuse array-zone or GSU point exposure. | included_v2_1_screening_reference | Mixed line-asset value; no qualified TC-wind curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!8 | SOLAR_VALUE_008_MV | Transformer, switches, breakers and substation | 106.50466417910448 | 2024_USD_per_kWdc | direct_hardware | PV_GSU_SUBSTATION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Reuse only asset-neutral GSU identity/value governance; never apply array exposure or inherit flood, solar-array wind, or wind-farm numerical response. | included_v2_1_screening_reference | Explicit GSU-substation candidate; shared anatomy does not provide a TC-wind curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!9 | SOLAR_VALUE_009_GROUNDING | Grounding and lightning protection | 8.385 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_COLLECTION | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not inherit array wind response; lightning is a separate pathway. | included_v2_1_screening_reference | Mixed grounding/lightning row.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!10 | SOLAR_VALUE_010_SCADA | System monitor | 1.31 | 2024_USD_per_kWdc | direct_hardware | PV_SCADA_COMMUNICATIONS | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Tracker control state may condition demand but is not a duplicate SCADA physical loss by default. | included_v2_1_screening_reference | No qualified direct TC-wind SCADA curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!11 | SOLAR_VALUE_011_NETWORK | Grid network upgrade | 0.0 | 2024_USD_per_kWdc | excluded_nonphysical | OUTSIDE_PHYSICAL_CELL | tropical_cyclone_wind | excluded | false | Exclude. | Never reintroduce through physical loss or support scaling. | excluded | Zero reference row.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!12 | SOLAR_VALUE_012_SBOS_LABOR | Mounting field labor | 43.273972602739725 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | tropical_cyclone_wind | included_support_once | false | Apply the value-weighted direct-and-civil DR once; do not damage support independently. | No intrinsic DR and no duplication inside failure-unit denominators or downstream support. | included_v2_1_derived_support_rule | Not all greenfield labor necessarily recurs; model v2.0 proposal scenario loss is withheld.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!13 | SOLAR_VALUE_013_EBOS_LABOR | Electrical field labor | 39.447761194029844 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | tropical_cyclone_wind | included_support_once | false | Apply the value-weighted direct-and-civil DR once; do not damage support independently. | Do not scale by array DR or charge across several electrical subjects by default. | included_v2_1_derived_support_rule | No independent curve; all associated direct electrical units are withheld.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!14 | SOLAR_VALUE_014_CIVIL | Grading, fencing, roads and buildings | 31.223744292237445 | 2024_USD_per_kWdc | mixed_civil_replacement_bucket | PV_CIVIL_INFRA | tropical_cyclone_wind | included_screening_direct_or_civil | true | Multiply the named row value by its v2.1 same-unit screening DR once. | Do not reuse array-zone exposure or structure DR. | included_v2_1_screening_reference | Mixed civil bucket; access/downtime is outside the physical curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!15 | SOLAR_VALUE_015_GENERAL_SUPPORT | Site management, equipment rental and inspection | 106.86876712328767 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | tropical_cyclone_wind | included_support_once | false | Apply the value-weighted direct-and-civil DR once; do not damage support independently. | Do not multiply independently by module, structure, GSU, or other unit DRs. | included_v2_1_derived_support_rule | No independent curve; model v2.0 proposal scenario loss is withheld.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!16-17 | SOLAR_VALUE_016_017_EXCLUDED | Officework and other soft/nonphysical value | 242.20429763733296 | 2024_USD_per_kWdc | excluded_soft_sunk_nonphysical | OUTSIDE_PHYSICAL_CELL | tropical_cyclone_wind | excluded | false | Exclude from the physical denominator unless a separate explicit insured-value contract says otherwise. | Never turn installed-TIV share into an intrinsic DR cap or reintroduce through support. | excluded | Installed 1120 minus physical 877.7957023626668.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_DIRECT | Direct hardware subtotal | 656.9814571503722 | 2024_USD_per_kWdc | reconciliation | ALL_DIRECT_FAILURE_UNITS | tropical_cyclone_wind | reference_only | false | Reconcile rows 2-10; never pool under one curve. | Candidate array units cover only module and mounting anatomy; withheld direct units remain unknown rather than zero. | reconciled_reference_only | Reference only; no model v2.0 proposal monetary loss.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_PHYSICAL | Physical replaceable reference basis | 877.7957023626668 | 2024_USD_per_kWdc | reconciliation | ALL_PHYSICAL_FAILURE_UNITS_AND_SUPPORT | tropical_cyclone_wind | reference_only | false | Physical reference equals direct hardware plus replacement/civil/support rows. | No pooled physical-base DR may bypass unit, exposure, withholding, or support-once rules. | v2_1_full_physical_reference_denominator | Withheld rows are unknown, not zero; no model v2.0 proposal monetary loss.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_INSTALLED | Installed CAPEX reference basis | 1120.0 | 2024_USD_per_kWdc | installed_reference | OUTSIDE_INTRINSIC_CURVE | tropical_cyclone_wind | reference_only | false | Reporting conversion only with an explicit numerator and denominator label. | Not an intrinsic curve denominator, cap, site default, or authorization for whole-plant exposure. | v2_1_installed_capex_reporting_denominator | Module plus mounting reference is 0.35821837273868046 of installed; value share is not DR.

## Parameter_Tiers
parameter | pathway_id | curve_id | value | param_role | tier | source_ids | reasoning | status | update_trigger
Perry_compatibility_source_derived_record_count | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | 1 | capability | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | One narrow noncanonical source-unit curve passes the screening gate. This count is scoped to the preserved Perry route, not the v2 package. | adopt | Promotion or model revision.
source_manual_csv_sha256 | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | edb34e74cc078bba1fdbe34463abadc794fd416caa66eb64ac3d0ed176ac5e00 | provenance_pin | T1_claims_or_field_calibrated | TCWS-S020 | Pins the exact reviewed source file. | adopt | Source file changes.
source_cohort_filter | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | mounting_type=ground AND tracking=false | selector | T1_claims_or_field_calibrated | TCWS-S020 | Separates the only adequately populated explicit architecture cohort. | adopt_with_limits | Architecture labels or source population changes.
source_cohort_n | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | 35 | sample_size | T1_claims_or_field_calibrated | TCWS-S020 | All fixed ground source-cohort records including the tail audit point. | adopt | Source changes.
runtime_fit_n | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | 34 | sample_size | T3_engineering_proxy_or_adjacent_empirical | TCWS-S020;GOVERNANCE_CONTRACT | Excludes the single 48.2 m/s sparse-tail observation. | adopt_with_limits | Tail evidence improves.
source_axis_id | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | PERRY_DATASET_REPORTED_EVENT_MAX_GUST_MPS | axis | T1_claims_or_field_calibrated | TCWS-S020;TCWS-S021 | Preserves the dataset-reported field without attributing one provider or inventing averaging, height, station, or query semantics for the full manual cohort. | adopt_with_limits | Source documentation clarifies the full manual-cohort weather lineage.
valid_range_mps | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | 17.4¦39.1 | boundary_or_cap | T3_engineering_proxy_or_adjacent_empirical | TCWS-S020;GOVERNANCE_CONTRACT | Source-bounded fit domain before the isolated severe-tail gap. | adopt_with_limits | Tail evidence improves.
fit_method | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | equal_record_weighted_PAVA_then_block_edge_linearization | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWS-S020;GOVERNANCE_CONTRACT | The 34 retained event/site records receive equal record weight; repeated physical sites mean this is not unique-site weighting. | adopt_with_limits | Reviewed predictive method replaces screening fit.
interpolation_policy | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | linear_between_source_knots | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | GOVERNANCE_CONTRACT | Continuous deterministic interpolation between governed block edges. | adopt_with_limits | Method revision.
extrapolation_policy | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | withhold outside 17.4-39.1 m/s | boundary_or_cap | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | No source-supported tail or low-end extrapolation. | adopt | New evidence expands range.
ordinate_percent_conversion | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | damage_ratio=pct_modules_damaged/100 | ordinate_bridge | T1_claims_or_field_calibrated | TCWS-S020;TCWS-S021 | Exact unit conversion from percent to fraction. | adopt | Source units change.
uniform_module_value | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | required_true | value_bridge | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | Makes module-count or equal-area fraction align with module-hardware value fraction. | adopt_with_limits | Observed module value distribution replaces assumption.
full_replacement_if_visible | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | required_true | disposition_bridge | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | Maps visible or missing module physical fraction to material replacement proxy. | adopt_with_limits | Inspected repair-versus-replace data replaces assumption.
extra_exposure_fraction | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | prohibited | exposure_modifier | T3_engineering_proxy_or_adjacent_empirical | TCWS-S020;TCWS-S021 | The site response already measures realized affected fraction. | adopt | Response grain changes.
Perry_compatibility_curve_intrinsic_spread | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | not_carried | uncertainty | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | Cluster-aware uncertainty is not identified by the sparse event sample. | withhold | Validated hierarchical uncertainty model.
tail_audit_point | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | 48.2 m/s¦0.4142383192 DR¦n=1 | audit_only | T1_claims_or_field_calibrated | TCWS-S020 | Retains the severe observation without granting runtime interpolation. | withhold_runtime | Tail cohort grows.
Perry_compatibility_model_grade | tropical_cyclone_wind | TCWS_PERRY_GROUND_FIXED_VISIBLE_REPLACEMENT_PROXY_V1 | screening_remote_sensing_labeled_visible_fraction_with_T4_economic_bridge | release_state | T4_placeholder_or_expert_judgment | TCWS-S020;GOVERNANCE_CONTRACT | Separates remote-sensing-labeled visible physical severity from assumed economic disposition. | adopt | Evidence chain improves.
TCWS21-P000 ¦ package curve-record count | tropical_cyclone_wind | CELL_CONTRACT | 10 | capability | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;GOVERNANCE_CONTRACT | One preserved Perry record, four architecture-specific array records, and five site-facility screening records. | adopted_model_v2_1 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2-P001 ¦ audit comparison profile | tropical_cyclone_wind | CELL_CONTRACT | SHARED_SOLAR_WIND_NORMALIZED_RESPONSE_SYNTHETIC_T4_V0_1 | provenance_pin | T4_placeholder_or_expert_judgment | SHARED_SOLAR_WIND_PROXY_V0_1;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | Audit-only byte-value comparison after cell-local adoption; never a runtime parameter source. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21-P000B ¦ array synthetic record count | tropical_cyclone_wind | CELL_CONTRACT | 4 | capability | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;GOVERNANCE_CONTRACT | Two fixed-tilt and two tracker array records remain unchanged from model v2.0. | adopted_model_v2_1 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2-P002 ¦ generic demand range | tropical_cyclone_wind | CELL_AXIS_CONTRACT | 0.0 to 2.0 | boundary_or_cap | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | The entire [0,2] interval is a bounded synthetic research domain with no internal evidence-anchored high-range threshold; values above 2 are withheld. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2-P003 ¦ hard-zero treatment | tropical_cyclone_wind | ALL_GENERIC_RECORDS | none above zero; exact x=0 only | curve_fit_shape | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | Avoid an invented immunity band and avoid intercept subtraction that changes parameter meaning. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21-P004 ¦ scenario physical loss | tropical_cyclone_wind | CELL_EMIT_CONTRACT | supported_with_named_reference_profile | value_linkage | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT;TCWS2-S013;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | Complete failure-unit screening coverage and the reconciled named value profile authorize explicit event physical loss; calibration grade remains Tier 4. | adopted_model_v2_1 | A governed value profile, calibrated unit curve, or output-contract revision changes this behavior.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.3 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS1_LOCALIZED_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.1 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS2_FIELD_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | [0.65, 1.2] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | [0.85, 1.55] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS2_FIXED_MODULE_SYNTHETIC_T4_ORDERED_STATES | [1.05, 1.95] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | 0.3 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | 0.15 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS2_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS3_TERMINAL_UNIT_FAILURE cost_ratio | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | [0.9, 1.2, 1.5] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | [1.15, 1.55, 1.9] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS2_FIXED_STRUCTURE_SYNTHETIC_T4_ORDERED_STATES | [1.45, 1.95, 2.35] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.275 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS1_LOCALIZED_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | 0.1 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ MODULE_DS2_FIELD_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | [0.8, 1.15] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | [0.95, 1.4] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS2_TRACKER_MODULE_SYNTHETIC_T4_ORDERED_STATES | [1.1, 1.7] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | 0.275 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | 0.15 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS2_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ STRUCT_DS3_TERMINAL_UNIT_FAILURE cost_ratio | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | [0.95, 1.15, 1.35] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | [1.15, 1.4, 1.65] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS2_TRACKER_SBOS_SYNTHETIC_T4_ORDERED_STATES | [1.35, 1.7, 2.0] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | 0.35 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ FOUNDATION_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ FOUNDATION_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | 0.05 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ FOUNDATION_DS2_MAJOR_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | 0.35 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ FOUNDATION_DS3_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | [0.84, 1.12, 1.44] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | [1.05, 1.4, 1.8] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS21_FOUNDATION_SCREENING_T4_ORDERED_STATES | [1.3125, 1.75, 2.25] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | 0.35 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ POWER_COLLECTION_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ POWER_COLLECTION_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | 0.1 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ POWER_COLLECTION_DS2_MAJOR_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | 0.4 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ POWER_COLLECTION_DS3_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | [0.72, 1.0, 1.32] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | [0.9, 1.25, 1.65] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS21_POWER_COLLECTION_SCREENING_T4_ORDERED_STATES | [1.125, 1.5625, 2.0625] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | 0.35 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ GSU_SUBSTATION_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ GSU_SUBSTATION_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | 0.08 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ GSU_SUBSTATION_DS2_MAJOR_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | 0.35 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ GSU_SUBSTATION_DS3_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | [0.76, 1.04, 1.36] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | [0.95, 1.3, 1.7] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS21_GSU_SUBSTATION_SCREENING_T4_ORDERED_STATES | [1.1875, 1.625, 2.125] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | 0.35 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ SCADA_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ SCADA_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | 0.15 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ SCADA_DS2_MAJOR_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | 0.55 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ SCADA_DS3_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | [0.6, 0.84, 1.16] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | [0.75, 1.05, 1.45] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_SCADA_SCREENING_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS21_SCADA_SCREENING_T4_ORDERED_STATES | [0.9375, 1.3125, 1.8125] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ beta_ln | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | 0.35 | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Synthetic log-space transition width; not fitted dispersion. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ CIVIL_DS0_NO_DIRECT_DAMAGE cost_ratio | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | 0.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ CIVIL_DS1_LOCALIZED_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | 0.08 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ CIVIL_DS2_MAJOR_REPAIR cost_ratio | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | 0.35 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ CIVIL_DS3_FULL_UNIT_REPLACEMENT cost_ratio | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | 1.0 | state_cost_ratio | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Explicit synthetic same-unit consequence ratio keeps probability and DR typed separately. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ lower_resistance medians | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | [0.64, 0.92, 1.28] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ central_screening medians | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | [0.8, 1.15, 1.6] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.
TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES ¦ upper_resistance medians | tropical_cyclone_wind | TCWS21_CIVIL_SCREENING_T4_ORDERED_STATES | [1.0, 1.4375, 2.0] | curve_fit_shape | T4_placeholder_or_expert_judgment | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | Unweighted synthetic resistance scenario; not a percentile or fitted hurricane parameter. | adopt_synthetic_T4 | Formal elicitation or matched TC field/claims calibration replaces this value.

## Sources
source_id | citation | url | accessed_on | exact_locator | source_type | source_role | pathway_ids | evidence_tier | target_asset_match | target_failure_unit_match | measured_or_modeled_endpoint | permitted_inference | prohibited_inference | decision | status | notes
TCWS-S001 | NOAA/National Hurricane Center. Glossary of NHC Terms: Maximum Sustained Surface Wind. | https://www.nhc.noaa.gov/aboutgloss.shtml | 2026-07-28 | entry: Maximum Sustained Surface Wind | government glossary | axis_bridge | tropical_cyclone_wind | T2_public_lab_standard_or_physics | none | none | highest one-minute average wind at 10 m in unobstructed exposure associated with the cyclone at a point in time | Define the source-native NHC storm-intensity quantity and require explicit height, averaging-period, terrain, gust, and local-demand bridges. | Treat storm category or maximum sustained surface wind as array-height component demand or damage without a qualified bridge. | adopt_with_limits | reviewed | Hazard semantics only; no curve or universal gust factor.
TCWS-S002 | Ceferino, L.; Lin, N.; Xi, D. Bayesian updating of solar panel fragility curves and implications of higher panel strength for solar generation resilience. Reliability Engineering & System Safety 229, 108896 (2023). DOI 10.1016/j.ress.2022.108896. | https://par.nsf.gov/servlets/purl/10481168 | 2026-07-28 | §2.1 and Table 1 pp. 2–3; §2.2 pp. 3–4; Eq. 1 and §3.1 p. 4; §4.2 and Figs. 5c/5d/6b p. 7 | peer-reviewed field-informed Bayesian fragility study | curve_fit_shape | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | probability that a large ground-mounted site has extensive structural failure, defined as clip/racking failure in more than 50% of panels, conditional on reconstructed 3-second gust; 14 Caribbean sites | Retain the source-native extensive-failure probability and posterior parameter summaries as a narrowly scoped candidate; preserve the 14-site population, reconstructed-wind uncertainty, composite limit state, and Bayesian parameter uncertainty. | Call probability economic DR; split the composite site limit state into module, fixed-rack, tracker, foundation, or electrical DR; transfer to a named CONUS architecture; use a deterministic curve made from posterior medians as the paper's posterior mean curve. | defer_candidate_only | reviewed | Ground-mounted posterior summaries: median v approximately 90 m/s, median beta approximately 0.15; these are audit candidates, not runtime parameters. Debris from damaged panels participated in observed cascades.
TCWS-S003 | Perry, K.; Jordan, D. C.; Nguyen, Q. Assessing the Impacts of Extreme Weather Events on Photovoltaic Installations Using Remote Sensing Imagery. Progress in Photovoltaics: Research and Applications 33(9), 1012–1023 (2025). DOI 10.1002/pip.70001; NREL/JA-5K00-92873. | https://www.osti.gov/pages/biblio/2574727 | 2026-07-28 | abstract p. 1012; §§2.1 and 2.4 pp. 1013–1016; §3.1 and Figs. 4–5/Table 2 pp. 1016–1018; Discussion pp. 1021–1022 | peer-reviewed field remote-sensing study with public DOE archive | case_study_severity | tropical_cyclone_wind | T1_claims_or_field_calibrated | partial | partial | visible post-event PV site damage and percent module area missing/damaged for 1,534 mixed residential, commercial, and utility sites after Hurricanes Maria and Irma, joined to third-party maximum gust estimates | Use as a fleet-scale visible-damage constraint, installation/mounting-data requirement, and field-data-program method; retain the reported weak gust-damage relationship and site heterogeneity. | Fit a utility-scale ground-mount curve from the aggregate; infer fixed-versus-tracker fragility, component disposition, hidden electrical damage, direct repair cost, or independence from the Ceferino Caribbean-event evidence. | adopt_with_limits | reviewed | Reported aggregate: 17% with visible hurricane damage and 2.8% with more than 50% visible damage. Mounting issues were proprietary for key paired sites; utility-scale subset is not separately calibrated.
TCWS-S004 | U.S. DOE Federal Energy Management Program; Elsworth, J.; Van Geet, O.; Robinson, G.; et al. Toward Solar Photovoltaic Storm Resilience: Learning from Hurricane Loss and Rebuilding Better (February 2023). | https://www.energy.gov/sites/default/files/2023-02/femp-toward-solar-pv-storm-resilience-learning-from-hurricane-loss-rebuilding-better_0.pdf | 2026-07-28 | Executive Summary pp. vi–vii; §1.1 and Table 1 pp. 2–3; §§2–2.1 pp. 5–6; §§3.1–3.6 pp. 7–12 | government-sponsored field investigation and engineering case study | case_study_severity | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | one 469 kW fixed-tilt St. Croix ground array assessed as total loss after Maria, with observed rack, clamp, fastener, corrosion, electrical-enclosure, water-ingress, and cascading mechanisms plus site-specific redesign analyses | Use to define failure units, construction/maintenance selectors, dependency chains, compound-peril boundaries, and exact-site engineering-review requirements. | Use the reported 104 mph event estimate or 145 mph design value as a population threshold; isolate wind-only economic loss; transfer the 12-degree rebuild tilt, pressures, or hardening benefit as universal modifiers. | adopt_with_limits | reviewed | The event combined high wind, wind-driven rain, and flash flooding; the report is one detailed case, not a pure-wind fragility dataset.
TCWS-S005 | ASCE/SEI 7-22. Minimum Design Loads and Associated Criteria for Buildings and Other Structures. | https://www.asce.org/publications-and-news/asce-7/ | 2026-07-28 | Ch. 26 wind-speed definitions and symbols; Ch. 29 §29.4.5; Ch. 31 §31.4.5 | consensus design standard | axis_bridge | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | design wind basis and ground-mounted fixed-tilt solar load provisions | Anchor design-basis lineage, 3-second gust semantics, risk category, exposure, and fixed-tilt demand normalization when the licensed project record confirms the exact edition and provisions. | Treat a code design wind as failure capacity, fragility median, economic loss state, or tracker aeroelastic qualification. | adopt_with_limits | reviewed | Official page confirms current standard identity; licensed normative text is not copied into the cell.
TCWS-S006 | FM. Property Loss Prevention Data Sheet 7-106: Ground-Mounted Solar Photovoltaic Power (April 2026). | https://www.fm.com/-/media/project/publicwebsites/fmglobal/documentum-new/data-sheet-individual/07-hazards/fmds07106.pdf | 2026-07-28 | §§2.1.2.1–2.1.2.4 pp. 2–4; §§3.1.1–3.1.2 pp. 10–12; Appendix B revision history p. 22 | insurer engineering guidance | selector_archetype | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | fixed-tilt design/wind-tunnel requirements; tracker third-party static, dynamic, and aeroelastic evaluation; site anemometers; operational stow trigger 25% below tested instability speed; debris-zone guidance | Require architecture-specific qualification, named instability test, anemometer/control evidence, and windborne-debris boundary fields. | Use 0.75 of tested instability speed as damage onset; use debris design-speed zones as fragility thresholds; assign numeric mitigation credit or economic DR. | adopt_with_limits | reviewed | The 25%-below value is an operational action margin, not a vulnerability ordinate.
TCWS-S007 | International Electrotechnical Commission. IEC 62817:2014+A1:2017, Photovoltaic systems—Design qualification of solar trackers. | https://webstore.iec.ch/en/publication/61127 | 2026-07-28 | official scope and product-detail page; tracker component and complete-system test-procedure description | international qualification standard | selector_archetype | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | design qualification and reported specification-sheet/test identity for solar trackers | Require exact tracker model, configuration, qualification edition, and test identity as selector metadata. | Infer site wind capacity, tropical-cyclone fragility, Ucrit for an unnamed tracker, stow reliability, or economic DR. | adopt_with_limits | reviewed | Qualification provenance is necessary but not sufficient for a damage curve.
TCWS-S008 | International Electrotechnical Commission. IEC 61730-2:2023 with COR1:2024, Photovoltaic module safety qualification—Part 2: Requirements for testing. | https://webstore.iec.ch/en/publication/63895 | 2026-07-28 | official scope, objective, test-sequence, and pass-criteria description; corrigendum status | international safety standard | selector_archetype | all_shared | T2_public_lab_standard_or_physics | direct | partial | PV module safety-qualification test requirements used with IEC 61730-1 | Record module qualification lineage and prevent unqualified module-class aliases. | Treat safety qualification as tropical-cyclone survival, module/rack structural fragility, wind-load capacity, or replacement-cost ratio. | adopt_with_limits | reviewed | Safety scope only; not a hurricane damage test.
TCWS-S009 | U.S. DOE/FEMP and GSA. PV System Owner's Guide to Identifying, Assessing, and Addressing Weather Vulnerabilities, Risks, and Impacts (2021). | https://www.energy.gov/sites/default/files/2021-09/pv-system-owners-guide-to-weather-vulnerabilities.pdf | 2026-07-28 | §5; PDF pp. 43–50 for clamps/racking and pp. 56–58 for high-wind field context | government field-audit guidance | mechanism_only | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | field-audit taxonomy for modules, clamps, fasteners, racking, wiring, enclosures, maintenance, and observed cascade mechanisms | Support candidate failure-unit coverage and selector/conditioner inspection fields. | Supply a numerical hurricane fragility, median, dispersion, component severity, or loss cap. | adopt_with_limits | reviewed | Reused from the governed strong_wind_solar evidence spine at qualitative mechanism grain only.
TCWS-S010 | Browne, M. T. L.; Taylor, Z. J.; Li, S.; Gamble, S. A wind load design method for ground-mounted multi-row solar arrays based on a compilation of wind tunnel experiments. Journal of Wind Engineering and Industrial Aerodynamics 205, 104294 (2020). DOI 10.1016/j.jweia.2020.104294. | https://doi.org/10.1016/j.jweia.2020.104294 | 2026-07-28 | abstract; §§1–5; limitations on flexible single-axis trackers | peer-reviewed atmospheric-boundary-layer wind-tunnel synthesis | axis_bridge | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | static and dynamic design wind coefficients for relatively rigid, fixed-tilt, multi-row ground-mounted arrays, including array zoning | Support a separate fixed-tilt demand bridge, perimeter/interior zoning, and small-deflection eligibility checks. | Transfer synoptic ABL coefficients to a tropical-cyclone site without basis; apply to flexible trackers; infer failure probability, damage state, or DR. | adopt_with_limits | reviewed | Strong-wind substrate reused at engineering-design grain; no numerical vulnerability transfer.
TCWS-S011 | Rodríguez-Casado, C.; Martínez-García, E.; Manzanares-Bercial, R.; et al. Experimental benchmark for the 3D wind tunnel testing of torsional aeroelastic instabilities in single-axis solar trackers. Journal of Wind Engineering and Industrial Aerodynamics 253, 105838 (2024). DOI 10.1016/j.jweia.2024.105838. | https://doi.org/10.1016/j.jweia.2024.105838 | 2026-07-28 | abstract; prototype and experimental-methodology sections; stability results; conclusions | peer-reviewed two-laboratory aeroelastic benchmark | axis_bridge | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | critical velocity for torsional instability of one defined 3D benchmark tracker by tilt and row position under controlled uniform-flow tests | Support exact-system Ucrit normalization and qualification metadata for a tracker-specific future bridge. | Use benchmark Ucrit as a generic production-tracker threshold, transfer uniform-flow results to a site TC field without qualification, or infer failure probability/economic DR. | adopt_with_limits | reviewed | Critical speed depends on the defined tracker and tilt; the source is not a population fragility.
TCWS-S012 | Frontini, G.; Calamelli, F.; Muggiasca, S.; Argentini, T. Key parameters influencing wind-induced aeroelastic responses of single-axis solar trackers in photovoltaic plants. Solar Energy 287, 113232 (2025). DOI 10.1016/j.solener.2024.113232. | https://doi.org/10.1016/j.solener.2024.113232 | 2026-07-28 | abstract; experimental/numerical method; stability map; stress envelopes; conclusions | peer-reviewed wind-tunnel and finite-element study | selector_archetype | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | tracker aeroelastic response and stress sensitivity to row position, pitch, wind direction/exposure angle, and ground-cover ratio | Require row/zone, angle, direction, layout, and structural-dynamic attributes for tracker routing. | Transfer tested critical speeds or angle ranking to another tracker, claim tropical-cyclone equivalence, or infer probability/severity/cost. | adopt_with_limits | reviewed | Architecture and conditioner evidence only.
TCWS-S013 | Ramasamy, V.; Woodhouse, M.; Feldman, D. Q1-2025 Solar Photovoltaic System Cost Benchmarks. NLR Data Catalog submission 304 (2025; updated 2026-01-06). DOI 10.7799/3009689. | https://data.nrel.gov/submissions/304 | 2026-07-28 | dataset landing page; UPV Q1-2025 resource; PVSCM 2025 model and description | official public cost dataset and model | exposure_or_value | all_shared | T2_public_lab_standard_or_physics | direct | partial | U.S. reference utility-scale PV component, balance-of-system, fieldwork, support, soft-cost, and installed-cost rows | Supply a row-level reference value ledger and denominator reconciliation after architecture/vintage/unit checks. | Infer fragility, damage probability, repair disposition, site replacement cost, exposed fraction, or support allocation. | adopt_with_limits | reviewed | Reference-value evidence only. The exact parent-ledger alias is value_source_id NLR_Q1_2025_UPV_PV_ONLY_2024_USD; that ledger governs rows, units, vintage, and support allocation.
TCWS-S014 | Du, X.; Becker, T.; Taylor, Z. J.; Needham, C. Cyclic Demands on Solar Structural Joints under Wind Loading. Journal of Structural Engineering 151(10), 04025156 (2025). DOI 10.1061/JSENDH.STENG-14435. | https://doi.org/10.1061/JSENDH.STENG-14435 | 2026-07-28 | abstract; Introduction; Prototype Structure; Wind Hazard Analysis; Conclusions | peer-reviewed CFD/FEA and wind-hazard study | mechanism_only | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | lifetime cyclic rotation demands for shared top-down clamps on a prototype fixed-tilt array under typical, explicitly non-hurricane winds | Support joint-condition, preload/installation, cyclic-demand, and cascading-dependency fields; demonstrate that equivalent-static design does not exhaust failure mechanisms. | Use the duty cycles as TC demand, a hurricane threshold, clamp failure probability, or repair-cost ratio. | adopt_with_limits | reviewed | The paper explicitly excludes extreme/hurricane winds from its hazard scenarios.
TCWS-S015 | Damage Modeling strong_wind_solar model-v2.0/docs-r1 proposed evidence package. | docs/cells/strong_wind_solar/proposed/SOURCE_REGISTER_strong_wind_solar__model_v2_0__docs_r1.csv | 2026-07-28 | rows DOE_PV_OWNER_GUIDE_2021, FIXED_TILT_WIND_DESIGN_2020, PV_TRACKER_AEROELASTIC_2024, TRACKER_LAYOUT_AEROELASTIC_2025, FM_DS_7_106_2026, ASCE_7_22, IEC_62817; neighboring-wind boundary memo | governed cross-cell evidence lineage | mechanism_only | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | previously reviewed solar anatomy, fixed-versus-tracker split, wind-demand mechanisms, and source transfer limits | Reuse source discovery, anatomy, terminology, and governance controls while independently registering primary sources here. | Inherit straight-line-convective axes, curves, T4 medians/beta/state costs, downburst profiles, or consumer behavior into tropical-cyclone wind. | adopt_with_limits | reviewed | Evidence reuse is not numerical model reuse.
LEG-TCWS-001 | InfraSure legacy HURRICANE x SOLAR research memo and master curve index. | infrasure-damage-curves/research/HURRICANE_x_SOLAR.md | 2026-07-28 | memo §§2.6–2.8, §5, §6, Appendix A; data/master_curve_index.json lines 219–299 | legacy research memo and curve index | rejected | tropical_cyclone_wind | T4_placeholder_or_expert_judgment | direct | partial | seven proposed ordinary-logistic subsystem records on 3-second gust mph, later presented as damage ratios | Use only for source discovery, numerical reproduction, defect audit, and migration regression fixtures. | Adopt any parameter, threshold, cap, confidence label, architecture shift, economic endpoint, or source characterization. | reject_runtime_retain_audit | reviewed | Pinned at legacy repository commit 12653b2c3d5a013c9524228243ea666c35bb3814; memo blob ea9febd74f91e79a41b5f7aca5ebd58d36a7230d; index blob 42e4b3d13d434322dd1e0c8d549d0e4b8167f28e. The memo misstates the Ceferino ground-mount posterior and converts a probability endpoint into capped DR.
LEG-TCWS-002 | Hazard Modeling hurricane-solar M3 provisional placeholder implementation. | Hazard_modeling/Notebooks/hurricane/solar/m3_damage/01_damage.py | 2026-07-28 | lines 14–39, 56–105, 136–183, and 197–207 | consumer code | rejected | tropical_cyclone_wind | T4_placeholder_or_expert_judgment | direct | partial | anchored legacy logistics blended with hardcoded full-TIV shares PV 0.35, mounting 0.15, substation 0.08, and remainder 0.42 assigned zero wind DR | Freeze exact behavior only as a migration/regression fixture and document downstream exposure/value assumptions. | Treat as scientific calibration, a governed Damage artifact, a valid capex denominator, or acceptable runtime fallback after the scaffold exists. | reject_runtime_retain_audit | reviewed | Pinned at Hazard_modeling commit 5033169cfed315dfe8575520a44f84404e89ecda; file blob d5cba3db1ed9f55bd2e8d1884b4a1f2fc144c3d2. It mixes aerodynamic, debris, rain, and generic substation proxies and calls absent coverage approximately wind-immune.
GOVERNANCE_CONTRACT | Damage Modeling repository governance: method standards, contracts, and damage-curve skill controls. | docs/method/standards/00_index.md | 2026-07-28 | docs/method/standards/02_cell_package_standard.md; docs/contracts/standards/20_machine_readable_artifact_standard.md; docs/contracts/standards/21_capability_and_cap_binding_standard.md; damage-curve skill CHANGE_CLASSIFIER and EVIDENCE_PRESSURE_TEST_AND_FAIL_CLOSED_CHECKLIST | internal governance control | governance_rule | all_shared | T4_placeholder_or_expert_judgment | direct | direct | change classification, provenance, pathway, seven-step, fail-closed, runtime-artifact, and reportability rules | Control package structure, source resolution, candidate isolation, withholding, event identity, and promotion gates. | Serve as scientific calibration, hazard evidence, or economic-value evidence. | adopt | reviewed | Internal authority for governance decisions only.
BOUNDED_SEARCH_LOG | Bounded evidence search log for tropical_cyclone_wind_solar model v0.1/docs r1. | docs/cells/tropical_cyclone_wind_solar/proposed/BOUNDED_EVIDENCE_SEARCH_LOG_tropical_cyclone_wind_solar__model_v0_1__docs_r1.md | 2026-07-28 | search cutoff, surfaces, exact query families, endpoint-chain matrix, limitations, and update triggers | governed search record | negative_evidence_boundary | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | direct | bounded result that no public matched tropical-cyclone demand-to-failure-unit-disposition-to-same-unit-cost chain was located within the recorded review | Support the scoped NO_RUNTIME_CURVE decision and define evidence-refresh triggers. | Claim universal absence across private owner/OEM/insurer data, non-indexed material, other languages, or evidence published after the cutoff. | adopt_with_limits | reviewed | Negative evidence is bounded, reproducible, and not universal.
TCWS-S020 | NLR/NREL. Satellite Imagery of PV Site Storm Damage. Dataset DOI 10.21948/2562917 (2025). | https://www.osti.gov/biblio/2562917 | 2026-07-28 | manual CSV file id f6eb09a0-4a12-4ef8-b2d9-8aa9e70f4008; columns mounting_type, tracking, max_wind_gust_(m/s), pct_modules_damaged (%); SHA256 edb34e74cc078bba1fdbe34463abadc794fd416caa66eb64ac3d0ed176ac5e00; aggregated CSV file id f5355652-f2e1-4bdb-8ff2-3623ce15a1d4; cross-method audit lines 7, 74, 242, 257; SHA256 c1ab48731f875142c571efcfd6323d7e048b35b2d2525418e25e6fefb3487062 | government research data archive | curve_fit_shape | tropical_cyclone_wind | T1_claims_or_field_calibrated | partial | direct_visible_module_proxy | 47 manually labeled sites; 37 ground; 35 ground non-tracking; percent visibly damaged module area and event maximum gust | Filter ground plus tracking false; convert percent to fraction; fit an unweighted monotone source-cohort screening relationship. Use the four pinned aggregate rows only for the governed apparent-coordinate cross-method audit. | Claim utility-scale representativeness, local 3-second gust semantics, causal purity, hidden damage, disposition, or repair cost from the raw fields. Treat coordinate proximity as an authoritative identity join. | adopt_with_limits | reviewed | Raw files are not redistributed because repository metadata states no license; DOI, file IDs, schemas, and hashes are pinned. The manual CSV alone enters the PAVA fit; aggregate rows are audit-only and never enter runtime fitting.
TCWS-S021 | NLR/NREL. Extreme Weather Data Description, file in Satellite Imagery of PV Site Storm Damage dataset DOI 10.21948/2562917. | https://www.osti.gov/biblio/2562917 | 2026-07-28 | data-description PDF file id f3736640-1433-42f6-bd0b-3e2bf9b2951e; pp. 1-2; SHA256 852ff0128c99e188127a3d789ab217f55c98dba4952db590e07c140bf45219d5 | government dataset documentation | endpoint_definition | tropical_cyclone_wind | T1_claims_or_field_calibrated | partial | direct_visible_module_proxy | manual site/damage polygons and aggregate percentage of modules blown away; Visual Crossing is documented for the aggregate Irma/Maria weather map but full manual-cohort weather-provider semantics remain unresolved | Define the observed physical fraction while preserving unresolved full-cohort weather-product lineage. | Invent gust provider, station, averaging period, height, exposure standard, module disposition, or economic denominator for the full manual cohort. | adopt_with_limits | reviewed | The manual and aggregate methods differ; the runtime fit uses only the manual CSV.
TCWS-S022 | Ceferino, L.; Lin, N.; Xi, D. Supplementary Information to Bayesian Updating of Solar Panel Fragility Curves and Implications of Higher Panel Strength for Solar Generation Resilience (2023). | https://ars.els-cdn.com/content/image/1-s2.0-S0951832022005117-mmc1.docx | 2026-07-29 | Supplementary Table 2 p. 4; SHA256 6a9e9f36e8e13ae2d9ea266258608a031fe6489bd31155f27b784f1ac7e06756 | peer-reviewed article supplement | cross_source_endpoint_audit | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | approximate percent of panels damaged at 14 Caribbean ground-mounted sites based mainly on reports and websites with visual satellite verification | Use as a cross-method same-event and same-site endpoint discrepancy and uncertainty challenge. | Pool with Perry, treat the approximate values as same-method or independent labels, or convert them to repair cost. | audit_only | reviewed | Matched-site values differ materially from Perry; the evidence is correlated by site/event and the supplement carries no paired site-level source gust table or same-unit cost.
TCWS-S023 | Visual Crossing. Weather Data Documentation. | https://www.visualcrossing.com/resources/documentation/weather-data/weather-data-documentation/ | 2026-07-29 | Wind section; windgust field; daily aggregation description | weather-provider technical documentation | axis_semantics_constraint | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | none | none | current provider definition of wind gust and daily maximum aggregation | Constrain what can and cannot be inferred from a Visual Crossing windgust field. | Assert that every historical Perry row is an exact 3-second gust at a fixed height/exposure or reconstruct the original query. | adopt_with_limits | reviewed | Vendor method evidence is not calibration authority.
TCWS-S024 | Visual Crossing. How Historical Weather Data Records Are Created from Local Weather Station Observations. | https://www.visualcrossing.com/resources/documentation/weather-data/how-historical-weather-data-records-are-created-from-local-weather-station-observations/ | 2026-07-29 | query-time station selection and hourly blending description | weather-provider technical documentation | axis_query_lineage_constraint | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | none | none | query-time construction from nearby station observations | Require archived station contributors and query settings before a source-to-Hazard bridge. | Treat a current vendor query as a reproducible copy of the Perry historical source field. | adopt_with_limits | reviewed | Perry's released rows omit contributor and query lineage.
TCWS-S025 | Walker, H. et al. Solar Photovoltaic System and Energy Storage System Field Assessments in Typhoon Mawar. NLR/TP-7A40-89629 (2024). DOI 10.2172/2479116. | https://www.nlr.gov/docs/fy25osti/89629.pdf | 2026-07-29 | Executive summary PDF pp. 4-6; report pp. 9-12, 18, 53, 78, 95-97; Tables 1-2 and 7; Figures 8 and A-2 | government field investigation | severe_fixed_tilt_audit_and_tracker_boundary | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | post-event inspected PV damage with estimated regional/site wind context | Use as a severe fixed-ground audit, installation-quality lesson, and explicit no-tracker boundary. | Pool with Perry, fit a tail, infer economic DR, or treat estimated wind as the Perry or Hazard axis. | audit_only | reviewed | Ground-module counts and some site wind summaries conflict within the report; author clarification is required before numerical ingestion.
TCWS-S026 | Li, A.; Wu, J. Quantitative assessment method of typhoon-induced photovoltaic damage and energy production losses: a case study of the 2024 Typhoon Yagi. Geomatics, Natural Hazards and Risk (2025). DOI 10.1080/19475705.2025.2569795. | https://doi.org/10.1080/19475705.2025.2569795 | 2026-07-29 | Methods Sections 2.1.2, 2.2.3-2.2.4; Eq. 8; Results and limitations | peer-reviewed regional remote-sensing study | regional_severe_event_audit | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | partial | none | satellite-observed PV-area disappearance joined to modeled 10 m wind-scale fields and generic unit area cost | Use as an external regional severity and data-design audit. | Transfer its wind scale, area loss, linear relation, or generic cost estimate into failure-unit economic DR. | audit_only | reviewed | Architecture, component state, disposition, and same-unit replacement value are unresolved.
TCWS-S027 | Li, Anqi; Wu, Jidong. Mapping results of photovoltaic solar panels in Hainan Island before and after Typhoon Yagi in 2024. Zenodo. DOI 10.5281/zenodo.15114346. | https://doi.org/10.5281/zenodo.15114346 | 2026-07-29 | dataset landing record and mapped before/after PV data | research data repository | regional_audit_data_lineage | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | partial | none | regional mapped PV extent used by the Yagi study | Preserve source lineage for the regional audit. | Treat mapped area disappearance as inspected module disposition or same-unit cost. | audit_only | reviewed | No row enters the Perry fit.
TCWS-S028 | Florida Power & Light Company. Direct Testimony of Michael A. Jarro, Docket 20240149-EI (2025). | https://www.psc.state.fl.us/library/FILINGS/2025/15505-2025/15505-2025.pdf | 2026-07-29 | PDF pp. 40-41 and footnote 9 | owner testimony filed with state regulator | field_occurrence_and_repair_actions | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | solar panel replacement, erosion/civil repair, aerial inspection, and fleet-level Milton panel damage fraction | Use as a censored occurrence bound and repair/inspection field-design evidence. | Convert the fleet panel fraction or pooled restoration total to site or failure-unit economic DR. | adopt_with_limits | reviewed | The exposed-site denominator, local intensity, architecture, and cause allocation are absent.
TCWS-S029 | Florida Power & Light Company. Direct Testimony of Amin Mohomed and Exhibit AM-3, Docket 20240149-EI (2025). | https://www.psc.state.fl.us/library/FILINGS/2025/15506-2025/15506-2025.pdf | 2026-07-29 | PDF pp. 19 and 29-30 | owner regulatory cost testimony | restoration_cost_scope_boundary | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | none | mixed generation restoration cost by contractor, logistics, material, labor, vehicle, and capitalization category | Demonstrate that support and restoration scope can be material and must be allocated once. | Treat a mixed PGD restoration bucket, capitalization share, or insurance position as solar economic DR. | adopt_with_limits | reviewed | The schedule spans preparation, inspection, logistics, civil work, and multiple generation facilities.
TCWS-S030 | Florida Power & Light Company. Hurricanes Ian and Nicole Final Actual Storm Amount Filing, Docket 20230017-EI (2023). | https://www.psc.state.fl.us/library/filings/2023/06108-2023/06108-2023.pdf | 2026-07-29 | Jarro testimony PDF pp. 45-47; Exhibit KF-1 PDF p. 106 | owner testimony and actual-cost filing with state regulator | field_occurrence_repair_and_cost_boundary | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | module, inverter, electrical-field, erosion, infrastructure, inspection actions and fleet panel-damage bound; pooled costs | Use physical actions and panel count bound for occurrence and acquisition design. | Allocate pooled generation costs to solar failure units or call panel fraction economic DR. | adopt_with_limits | reviewed | Under 0.04 percent of FPL panels were reported damaged by Ian; exact exposed subset and local wind are absent.
TCWS-S031 | Florida Power & Light Company. Prepared Testimony of Brandon J. Stankiewicz Supporting the 2027 Solar Base Rate Adjustment, Docket 20260001-EI (2026). | https://www.psc.state.fl.us/library/filings/2026/02016-2026/02016-2026.pdf | 2026-07-29 | PDF pp. 5-6; solar anatomy pp. 7-14 | owner testimony filed with state regulator | fleet_exposure_and_replacement_bound | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | 66 of 89 utility-scale sites exposed and fewer than 0.07 percent of panels required replacement across stated events | Use as a fleet-level censored replacement-count observation and asset-anatomy input. | Infer site-level vulnerability, event-specific DR, architecture effect, or direct cost. | adopt_with_limits | reviewed | Two-event scope and panel denominator wording remain ambiguous.
TCWS-S032 | FEMA. Mitigation Assessment Team Report: Hurricanes Irma and Maria in the U.S. Virgin Islands (2018). | https://www.fema.gov/sites/default/files/documents/fema_mat-report_hurricane-irma-maria_virgin-islands.pdf | 2026-07-29 | Section 7.1.2 pp. 7-5-7-7; Section 7.1.3 pp. 7-7-7-9 | government forensic field investigation | fixed_tilt_failure_unit_occurrence | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | site wind estimates and observed module, post, purlin, connector, rack, and facility states | Use as architecture-specific physical mechanism and inspected-state evidence. | Convert module/post fractions, qualitative total damage, or estimated wind into same-unit economic DR. | adopt_with_limits | reviewed | No repair invoice and matching pre-event replacement-value schedule are supplied.
TCWS-S033 | BMR Energy. St. Thomas Solar Project. | https://bmrenergy.com/projects/st-thomas-solar-project/ | 2026-07-29 | Context and Process sections | asset owner project record | final_disposition_and_rebuild_context | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | original facility removal and redesigned replacement after hurricane damage | Use as owner-reported terminal facility disposition and rebuild-selector evidence. | Treat redesigned, resized, and hardened replacement scope as like-kind direct repair cost. | adopt_with_limits | reviewed | The replacement facility is not a same-unit economic denominator for the original plant.
TCWS-S034 | BMR Energy. St. Croix Solar Energy. | https://bmrenergy.com/projects/st-croix-solar-energy/ | 2026-07-29 | Context and Process sections | asset owner project record | module_and_electrical_disposition_context | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | limited module/rack repair and replacement of moisture/static-damaged inverter/electrical equipment | Use to show visible module damage can underrepresent electrical consequence and compound pathways. | Infer component quantities, wind-only causation, or economic DR. | adopt_with_limits | reviewed | No component cost allocation or pre-event replacement value is published.
TCWS-S035 | The AES Corporation. Form 10-Q for quarter ended September 30, 2017. | https://www.sec.gov/Archives/edgar/data/874761/000087476117000066/q32017form10-q.htm | 2026-07-29 | lines 2131-2140 and 3507-3513 in SEC filing text | issuer regulatory filing | plant_loss_materiality_and_scope_boundary | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | none | estimated plant-level hurricane losses and availability statements | Use as plant-level materiality and prohibited-numerator evidence. | Treat estimated loss, MW-normalized loss, availability reduction, insurance coverage, BI, cleanup, or recovery as direct physical DR. | audit_only | reviewed | No same-unit direct-cost allocation or replacement-value denominator is disclosed.
TCWS-S036 | DOE/FEMP, GSA, NREL, and LBNL. Toward Solar Photovoltaic Storm Resilience: Learning from Hurricane Loss, Rebuilding Better. | https://www.energy.gov/sites/default/files/2023-02/femp-toward-solar-pv-storm-resilience-learning-from-hurricane-loss-rebuilding-better_0.pdf | 2026-07-29 | PDF pp. 9-15 and 24; site assessments, Table 1, failure analysis, and hardening discussion | government in-person field investigation | multi_failure_unit_and_compound_event_evidence | tropical_cyclone_wind | T1_claims_or_field_calibrated | direct | partial | inspected module, rack, conduit, inverter, switchgear, transformer, water-ingress, and facility dispositions | Use for failure-unit anatomy, categorical disposition, compound-pathway boundaries, and acquisition design. | Serialize total-loss wording or hardening premiums as a transferable wind economic DR point. | adopt_with_limits | reviewed | Wind, wind-driven rain, flooding, and installation/design weaknesses are intertwined; no same-unit occurrence cost/value pair is supplied.
TCWS-S037 | NREL. Solar Photovoltaics in Severe Weather: Cost Considerations for Storm Hardening PV Systems for Resilience. NREL/TP-7A40-75804 (2020). DOI 10.2172/1659785. | https://doi.org/10.2172/1659785 | 2026-07-29 | PDF pp. 8-13; Tables 1-2 | government engineering and cost study | design_anatomy_and_hardening_cost_boundary | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | new-build BOM and prospective severe-weather hardening cost premiums | Use for design selectors, value anatomy, and data-acquisition fields. | Treat prospective premium or BOM share as occurrence damage probability, DR, or repair savings. | adopt_with_limits | reviewed | Repair savings are not quantified.
TCWS-S038 | Nextracker. Solar Power Plant O&M in the Age of Extreme Weather (2017). | https://www.nextracker.com/wp-content/uploads/2017/04/Nextracker_OandM-WhitePaper_FINAL_April-2017_MKT-000059.pdf | 2026-07-29 | printed p. 9, Hurricane Matthew case | OEM engineering case record | tracker_state_candidate_evidence | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | claimed tracker stow state and survival during a hurricane | Use as candidate attained-state and inspection-field design evidence. | Infer a generic tracker zero curve, stow credit, response probability, or economic DR. | audit_only | reviewed | No site inventory, local wind lineage, inspection protocol, or cost is published.
TCWS-S039 | Nevados. Iris Solar Project Hurricane Case Study. | https://nevados.solar/featured-projects/iris-case-study-hurricane/ | 2026-07-29 | Hurricane Ida event and post-event inspection sections | OEM owner-facing case record | tracker_occurrence_audit | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | claimed no structural tracker damage with limited lightning/debris module replacement | Use as a tracker negative-case and compound-attribution design input. | Infer wind-only immunity, a generic tracker curve, or repair-cost severity. | audit_only | reviewed | Self-published and missing inventory, local demand, component counts, direct cost, and replacement value.
TCWS-S040 | DOE/FEMP. Life Cycle of Photovoltaic Systems: Operate and Maintain an Existing Photovoltaic System. | https://www.energy.gov/cmei/femp/life-cycle-photovoltaic-systems-operate-and-maintain-existing-photovoltaic-system | 2026-07-29 | post-damage inspection, itemized repair-or-replace, and severe-storm model limitations in lines 143-190 | government operations guidance | inspection_and_disposition_protocol | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | recommended post-damage testing, itemized repair/replace scope, and estimate workflow | Use to define minimum inspection and disposition records. | Treat the O&M model or guidance as a severe-storm vulnerability curve. | adopt_with_limits | reviewed | The guidance states its O&M model does not estimate severe-storm damage.
PV_TRACKER_DOWNBURST_2025 | Álvarez et al. Downburst-Induced Loads on a Six-Row Array of Ground-Mounted Solar Trackers. Proceedings of the 10th International Conference on Advances in Experimental Structural Engineering, 2025. | https://doi.org/10.1007/978-3-031-98893-6_6 | 2026-07-12 | pp. 54–63; §§2–6; especially pp. 57–62 | peer-reviewed conference experiment | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 1:20 six-row rigid tracker model; 576 pressure taps; eight vertical-jet downburst repeats; pressure-time histories | Transient ramp/plateau/decay, primary-vortex surge, row and tilt dependence, downburst knowledge gap | Critical speed, component capacity, failure probability, damage state, economic DR, full-scale threshold | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
IEA_PVPS_EXTREME_WEATHER_2025 | IEA PVPS Task 13. Operational and Economic Impacts of Extreme Weather on PV Power Plants. T13-33:2025. | https://iea-pvps.org/wp-content/uploads/2025/12/IEA-PVPS-T13-33-2025-REPORT-Extreme-Weather-Impacts.pdf | 2026-07-12 | §3.2.2 pp. 24–25; §§3.4–3.6 pp. 25–28 | international laboratory synthesis | adjacent_normalized_response_anatomy_only | all_shared | T3_engineering_proxy_or_adjacent_empirical | direct | partial | reported straight-line wind cases around 22–28 m/s; Oakey and Lamar tracker narratives | Observed below-design damage is possible; 1P/2P, stow, perimeter and anemometer state are load-bearing | Population fragility, normalized DR, exact value denominator, literal threshold or fitted median; Lamar citation is uncertain | retain_as_adjacent_or_T4_context | reviewed | RETAINED_AS_SCREENING_CONSTRAINT
VALENTIN_TRACKER_FAILURE_2022 | Valentín et al. Failure Investigation of a Solar Tracker Due to Wind-Induced Torsional Galloping. Engineering Failure Analysis 135, 106137 (2022). | https://doi.org/10.1016/j.engfailanal.2022.106137 | 2026-07-12 | §§3.2–3.3, 4.3 and 6 | peer-reviewed forensic case | adjacent_normalized_response_anatomy_only | all_shared | T3_engineering_proxy_or_adjacent_empirical | direct | partial | one exposed flat tracker failed; nearby station about 16.7 m/s; rotation, module, shaft and pillar damage | Tracker cascade sequence and importance of angle/exposure | Convective attribution, local threshold, population probability, economic DR | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
CPP_TRACKER_INSTABILITY_2015 | Rohr, Bourke and Banks. Torsional Instability of Single-Axis Solar Tracking Systems. 2015. | https://www.cppwind.com/wp-content/uploads/2020/12/Torsional-Instability-of-Single-Axis-Solar-Tracking-Systems-Rohr-Bourke-Banks-2015.pdf | 2026-07-12 | pp. 1–7; especially pp. 5–7 | engineering wind-tunnel / CFD paper | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | sectional critical velocity and tracker twist under ABL flow | System-specific critical-speed and angle-conditioned tracker axis | Universal 40 m/s threshold, downburst response, DR or loss | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
TRACKER_LAYOUT_AEROELASTIC_2025 | Frontini et al. Key Parameters Influencing Wind-Induced Aeroelastic Responses of Single-Axis Solar Trackers in Photovoltaic Plants. Solar Energy 2025, 113232. | https://doi.org/10.1016/j.solener.2024.113232 | 2026-07-12 | abstract; stability map Fig. 7; stress envelopes Fig. 12 | peer-reviewed wind-tunnel and FEM study | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | critical response by tracker position, pitch, direction and ground-coverage ratio | Required row, pitch, direction and layout fields | Transfer of tested critical speeds to another tracker or to downburst loading | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
PV_TRACKER_AEROELASTIC_2024 | Rodríguez-Casado et al. Experimental Benchmark for the 3D Wind Tunnel Testing of Torsional Aeroelastic Instabilities in Single-Axis Solar Trackers. JWEIA 2024, 105838. | https://doi.org/10.1016/j.jweia.2024.105838 | 2026-07-12 | abstract and §§1–3 | peer-reviewed aeroelastic benchmark | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 3D aeroelastic critical velocity by design and tilt in two tunnels | Exact-system named Ucrit normalization and qualification identity | Generic production-tracker fragility or damage probability | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
TRACKER_FIELD_MODAL_2024 | Koekemoer et al. Field Measurements of Wind Load Effects in a Photovoltaic Single-Axis Tracker Mounting Rail. JWEIA 2024, 105876. | https://doi.org/10.1016/j.jweia.2024.105876 | 2026-07-12 | abstract; 109-day campaign | peer-reviewed full-scale field measurements | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 1P tracker torsional and bending modal response by direction and pile position | 1P/2P and modal/layout differentiation | No-damage threshold or destructive convective response | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
FIXED_TILT_WIND_DESIGN_2020 | Browne et al. A Wind Load Design Method for Ground-Mounted Multi-Row Solar Arrays Based on a Compilation of Wind Tunnel Experiments. JWEIA 2020, 104294. | https://doi.org/10.1016/j.jweia.2020.104294 | 2026-07-12 | abstract and §§1–5 | peer-reviewed ABL wind-tunnel synthesis | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | fixed-tilt static/dynamic pressure coefficients and perimeter/field zones | Separate fixed-tilt load bridge and array zoning | Downburst coefficients, tracker aeroelasticity, failure probability or DR | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
SOLAR_JOINT_CYCLIC_2025 | Du et al. Cyclic Demands on Solar Structural Joints under Wind Loading. Journal of Structural Engineering, 2025. | https://doi.org/10.1061/JSENDH.STENG-14435 | 2026-07-12 | abstract and conclusions | peer-reviewed CFD/FEA/hazard study | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | lifetime clamp/joint cyclic demand | Joint coverage and acute-versus-fatigue boundary | Single-occurrence convective DR or lifetime-to-peak conversion | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
SOLAR_CRITICAL_JOINTS_2025 | Robinson. Maturing Rational Design Methodologies and Industry Consensus Engineering Standards: Critical Fastened Joints – Solar PV Industry. LBNL, 2025. | https://doi.org/10.20357/B7VG76 | 2026-07-12 | abstract and report | public-laboratory engineering report | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | joint failure, racking deflection/twist and load feedback | Attachment/joint condition and cascade logic | Wind-to-failure population or cost fraction | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
DOE_PV_OWNER_GUIDE_2021 | U.S. DOE/FEMP and GSA. PV System Owner’s Guide to Identifying, Assessing, and Addressing Weather Vulnerabilities, Risks, and Impacts. 2021. | https://www.energy.gov/sites/default/files/2021-09/pv-system-owners-guide-to-weather-vulnerabilities.pdf | 2026-07-12 | §5; PDF pp. 43–50 for clamps/racking; derecho context pp. 56–58 | official field-audit guidance | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | field-audit vulnerabilities and observed module, clamp, fastener, racking, wiring and enclosure mechanisms | Failure-unit coverage, dependency, audit and conditioner fields | Numerical utility-scale convective fragility, parameter median, dispersion or loss cap | retain_as_adjacent_or_T4_context | reviewed | RETAINED_QUALITATIVE
NREL_WEATHER_IMPACTS_2021 | Walker et al. Weather Impacts on Solar PV Operations: Summary of the 2021 PV Reliability Workshop. LBNL/NREL/Sandia, 2021. | https://escholarship.org/content/qt5t8569hf/qt5t8569hf_noSplash_f0e76891c1cd44233507d7c5afbad87a.pdf | 2026-07-12 | pp. 23–25, 30–32, 39–42 and 56–58 | public-laboratory workshop synthesis | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | field cases, clamp/fastener failure, module/rack dynamics, thunderstorm/downburst context | Mechanism, dependency, below-design failure possibility and open evidence seams | Curve calibration, universal threshold or repair-cost ratio | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
FM_DS_7_106_2026 | FM. Data Sheet 7-106: Ground-Mounted Solar Photovoltaic Power. April 2026. | https://www.fm.com/-/media/project/publicwebsites/fmglobal/documentum-new/data-sheet-individual/07-hazards/fmds07106.pdf | 2026-07-12 | §§2.1.2.3–2.1.2.4 pp. 3–4; §3.1 pp. 10–11 | insurer engineering standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | static/dynamic/aeroelastic review; multiple anemometers; stow trigger 25% below tested instability speed | Ucrit qualification, monitoring and 0.75 action flag | 0.75 as damage threshold, hard zero or fragility ordinate | retain_as_adjacent_or_T4_context | reviewed | RETAINED_AS_GATE_NOT_CURVE
ASTM_E1830_2025 | ASTM E1830-15(2025). Standard Test Methods for Determining Mechanical Integrity of Photovoltaic Modules. | https://store.astm.org/e1830-15r25.html | 2026-07-12 | scope §§1.1–1.4; significance §4 | consensus test standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 2400 Pa static, 1440 Pa cyclic, twist test; no pass/fail level | Module qualification metadata and physical/electrical endpoints | Universal wind speed, failure probability or economic DR | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
IEC_62782_2016 | IEC TS 62782:2016. Photovoltaic modules — Cyclic (dynamic) mechanical load testing. | https://webstore.iec.ch/en/publication/24310 | 2026-07-12 | scope | international test standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | alternating uniform module load test | Module-test provenance and fatigue susceptibility | Transient downburst, plant fragility or DR | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
IEC_62817 | IEC 62817:2014+A1:2017. Photovoltaic systems — Design qualification of solar trackers. | https://webstore.iec.ch/en/publication/61127 | 2026-07-12 | scope and qualification sequence | international qualification standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | tracker design qualification | Exact tracker architecture/qualification identity and testing context | Site-specific structure/foundation certification, Ucrit for an unnamed tracker, or fragility | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
ASCE_7_22 | ASCE/SEI 7-22. Minimum Design Loads and Associated Criteria for Buildings and Other Structures. | https://www.asce.org/publications-and-news/codes-and-standards/asce-sei-7-22 | 2026-07-12 | Ch. 29 §29.4.5; Ch. 31 §31.4.5; Ch. 26 symbols | consensus design standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | fixed-tilt ground-mount wind design; 3-second gust at 10 m Exposure C source definition | Design normalization and fixed-tilt scope | Failure capacity, D50, tracker aeroelastic response or downburst profile | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
ASCE_49_21 | ASCE/SEI 49-21. Wind Tunnel Testing for Buildings and Other Structures. | https://www.asce.org/communities/institutes-and-technical-groups/structural-engineering-institute/committees/sei-board-of-governors/sei-technical-community-executive-committee/asce-49---wind-tunnel-testing | 2026-07-12 | §2.3.2 nonsynoptic winds | consensus wind-tunnel standard | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | wind-tunnel requirements including downbursts and other nonsynoptic winds | Named downburst/non-synoptic and tracker qualification bridge | PV fragility or damage parameters | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
NIST_THUNDERSTORM_PROFILES_2011 | Lombardo et al. Thunderstorm Characteristics of Importance to Wind Engineering Part II: Profiles, Gust Factors and Other Observations. JWEIA 2011. | https://www.nist.gov/publications/thunderstorm-characteristics-importance-wind-engineering-part-ii-profiles-gust-factors | 2026-07-12 | abstract and paper; ramp-up/profile/gust-factor sections | peer-reviewed primary field analysis | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | nonstationary ramp-up, vertical components, profile and gust-factor variability | Reject silent stationary-ABL equivalence and ordinary default profile conversion | Solar failure threshold or DR | retain_as_adjacent_or_T4_context | reviewed | RETAINED
FULL_SCALE_DOWNBURST_2018 | Gunter and Schroeder. Investigation of a Downburst Loading Event on a Full-Scale Low-Rise Building. JWEIA 2018. | https://doi.org/10.1016/j.jweia.2018.09.020 | 2026-07-12 | highlights and results | peer-reviewed full-scale event study | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | about 30 s ramp; peak near 4 m; direction change up to about 30° over 50 m | Rise time, direction change and non-power-law bridge requirement | PV fragility or structural transfer coefficients | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_ASSET_TRANSFER_LIMIT
DERECHO_MULTISCALE_2025 | Wagner et al. Detecting and Interpreting Wind Damage at Multiple Scales in the 10 August 2020 Derecho Using UAS, Satellite, and Radar. Weather and Forecasting, 2025. | https://doi.org/10.1175/WAF-D-24-0198.1 | 2026-07-12 | abstract; pp. 1–2 and 12–14 | peer-reviewed event reconstruction | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | MCS flow, downburst clusters, mesovortices, tornadoes and roughly 10 m damage variability | Derecho label requires local mechanism partition and parent event identity | One derecho-wide demand or PV parameter | retain_as_adjacent_or_T4_context | reviewed | RETAINED
NWS_DOWNBURST_TAXONOMY | U.S. National Weather Service. Downbursts; NWS Glossary; NSSL Thunderstorm FAQ. | https://www.weather.gov/spotterguide/downbursts | 2026-07-12 | definitions | official meteorological definitions | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | downburst, microburst, macroburst, gust front and derecho taxonomy | Pathway scope vocabulary | 58 mph warning threshold as PV damage onset | retain_as_adjacent_or_T4_context | reviewed | RETAINED
DOE_FEMP_STORM_HARDENING_2020 | Elsworth and Van Geet. Solar Photovoltaics in Severe Weather: Cost Considerations for Storm Hardening PV Systems for Resilience. NREL/TP-7A40-75804, 2020. | https://docs.nrel.gov/docs/fy20osti/75804.pdf | 2026-07-12 | Table 1 pp. 2–3; scope pp. 3–4 | public-laboratory cost report | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | incremental preventive costs for fasteners, through-bolts, modules, rails, piers and racking | Selector economics and plausibility only | Repair cost, damage-state ratio, tracker value or fragility | retain_as_adjacent_or_T4_context | reviewed | RETAINED_WITH_TRANSFER_LIMIT
NREL_Q1_2021_COST_BENCHMARK | Ramasamy et al. U.S. Solar Photovoltaic System and Energy Storage Cost Benchmarks: Q1 2021. NREL/TP-7A40-80694. | https://www.govinfo.gov/content/pkg/GOVPUB-E9-PURL-gpo184395/pdf/GOVPUB-E9-PURL-gpo184395.pdf | 2026-07-12 | PDF p. 27 utility-scale modeling inputs | public-laboratory cost benchmark | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | structural components 0.09–0.12 2020 USD/Wdc for fixed tilt or one-axis tracking | Fixed-tilt screening value bracket | Architecture-specific point value, fragility or current-dollar replacement cost | retain_as_adjacent_or_T4_context | reviewed | RETAINED_AS_RANGE_ONLY
NREL_Q1_2024_MMP_TRACKER | DOE/NREL PV System Cost Model Q1 2024 market price benchmark for a 100 MWdc one-axis-tracker plant. | https://www.energy.gov/cmei/systems/solar-photovoltaic-system-cost-benchmarks | 2026-07-12 | Figure 1 source-native MMP rows | public-laboratory cost benchmark | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 336 module, 140 SBOS, 33 inverter, 186 EBOS, 229 fieldwork, 1119 total; 2023 USD/kWdc | Tracker architecture sensitivity and row-level reconciliation | Fixed-tilt point value, component fragility or blended primary reference | retain_as_adjacent_or_T4_context | reviewed | RETAINED_FOR_VALUE_ONLY
NREL_NLR_Q1_2025_PV_BENCHMARK | Basore et al. Q1-2025 Solar Photovoltaic System Cost Benchmarks. NLR/OT-7A40-97930; data catalog submission 304. | https://doi.org/10.7799/3009689 | 2026-07-12 | dataset and governed Solar_Map crosswalk | official cost dataset | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 2024 USD/kWdc utility-PV installed and value rows | Repository-current reference-value reconciliation | Site appraisal, architecture-specific BOM, vulnerability or exposed fraction | retain_as_adjacent_or_T4_context | reviewed | RETAINED_FOR_VALUE_ONLY
VALUE_SOLAR_WORKBOOK | damage_modeling/docs/method/value_basis/solar_wind_value_breakdown.xlsx. | https://data.nlr.gov/submissions/304 | 2026-07-12 | Solar_Map rows 2–17 | internal governed derivation | adjacent_normalized_response_anatomy_only | all_shared | T2_public_lab_standard_or_physics | direct | partial | 2024 USD/kWdc row-level direct, support and excluded values | Reference denominator and row mapping | Implicit site value, at-risk fraction or fragility | retain_as_adjacent_or_T4_context | reviewed | RETAINED_FOR_REFERENCE_ONLY
LEGACY_SWS_V1 | Current canonical strong_wind_solar model v1.0/docs r3 artifact and workbook. |  | 2026-07-12 | docs/cells/strong_wind_solar/current/ | legacy implementation audit | adjacent_normalized_response_anatomy_only | all_shared | T4_placeholder_or_expert_judgment | direct | partial | gust mph, effective demand ratio, five logistics and value shares | Exact legacy reproduction and migration comparison | Scientific calibration for v2 | retain_as_adjacent_or_T4_context | reviewed | REJECTED_FOR_CALIBRATION
SHARED_SOLAR_WIND_PROXY_V0_1 | Damage Modeling shared solar-wind normalized-response candidate profile v0.1. | docs/method/shared_components/solar_wind_normalized_response/candidate_response_profile_v0_1.json | 2026-07-29 | complete non-runtime candidate profile | internal governed synthetic scenario substrate | audit_comparison_profile_only | all_shared | T4_placeholder_or_expert_judgment | direct | direct | unweighted normalized-demand state-response envelope | Compare cell-local synthetic parameters against a hazard-label-neutral solar fingerprint after adoption. | Call the values field-calibrated, hurricane-calibrated, conservative, probabilistic, or runtime approved. | retain_audit_only | reviewed_nonruntime | Standard 20 prohibits this candidate from populating an output-bearing cell bundle.
TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | Damage Modeling owner decision: TC-wind x solar model-v2 cell-local synthetic parameter set. | docs/cells/tropical_cyclone_wind_solar/proposed/DECISION_LOG_tropical_cyclone_wind_solar__model_v2_0__docs_r1.md | 2026-07-29 | TCWS2-D001; TCWS2-D003 through TCWS2-D007 | governed owner assumption decision | cell_local_synthetic_parameter_authority | tropical_cyclone_wind | T4_placeholder_or_expert_judgment | direct | direct | owner-adopted unweighted normalized-demand state/DR scenarios | Use the exact registered values only in this noncanonical v2 cell proposal. | Treat the decision as evidence, calibration, shared-runtime approval, or authority for another cell. | adopt_cell_local_synthetic_T4 | reviewed_noncanonical | Byte-equal comparison to the audit profile is intentional but is not a runtime dependency.
NO_DIRECT_TC_CALIBRATION_SOURCE | TC-wind x solar model-v2 bounded evidence review: no direct generic fixed/tracker calibration source adopted. | docs/cells/tropical_cyclone_wind_solar/proposed/BOUNDED_EVIDENCE_SEARCH_LOG_tropical_cyclone_wind_solar__model_v2_0__docs_r1.md | 2026-07-29 | § Missing matched chain; § v2 consequence | governed negative evidence finding | no_direct_calibration_marker | tropical_cyclone_wind | T4_placeholder_or_expert_judgment | direct | direct | absence of an adopted matched TC demand-state-cost-value calibration | Keep all generic numbers at Tier 4 and promotion blocked. | Infer zero damage, immunity, or proof that no usable private evidence exists. | withhold_calibration_claim | reviewed | This marker is TC-specific and does not reuse the convective-wind negative-search record.

## Claims
claim_id | pathway_id | claim_text | claim_type | source_ids | exact_locator | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
TCWS-C001 | tropical_cyclone_wind | Tropical-cyclone wind requires its own solar pathway and cannot fall back to the straight-line-convective solar model. | governance_decision | TCWS-S015;GOVERNANCE_CONTRACT | strong_wind_solar neighboring-wind boundary; pathway and event-identity standards | T3_engineering_proxy_or_adjacent_empirical | pathway_id=tropical_cyclone_wind | adopt | Reuse governed solar anatomy, terminology, and value lineage after a new transfer review. | Reuse a convective curve, axis, downburst profile, or numeric parameter because both pathways involve wind. | Storm duration, direction history, profile, turbulence, debris environment, and control opportunity differ and remain load-bearing. | A reviewed equivalence study passes all pathway and endpoint gates.
TCWS-C002 | tropical_cyclone_wind | NHC maximum sustained surface wind is the highest one-minute average wind at 10 m in unobstructed exposure. | direct_observation | TCWS-S001 | NHC glossary entry: Maximum Sustained Surface Wind | T2_public_lab_standard_or_physics | source_native_axis_semantics | adopt | Label the upstream storm-field quantity and retain its source product, valid time, height, averaging period, and exposure convention. | Treat it as array-height 3-second gust, tracker-normal wind, net pressure, or damage demand. | The official source defines the storm quantity but supplies no universal site or array bridge. | NHC changes the definition or a governed upstream product supplies a different exact convention.
TCWS-C003 | tropical_cyclone_wind | The runtime damage axis is withheld at scaffold stage. | governance_decision | TCWS-S001;TCWS-S002;TCWS-S005;TCWS-S010;TCWS-S011;GOVERNANCE_CONTRACT | native-axis definitions and transfer limits; runtime gate | T3_engineering_proxy_or_adjacent_empirical | runtime_axis_status | historical_scope_only | Preserve source-native axes and document architecture-specific bridge requirements. | Publish a silent one-minute-to-three-second, height, terrain, direction, pressure, or Ucrit conversion. | Available sources use different storm, local gust, pressure, and exact-system instability quantities. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C002/008/009; the underlying evidence limitation is retained. | A qualified event-to-local-demand bridge and matching damage evidence pass review.
TCWS-C004 | tropical_cyclone_wind | Height, averaging period, terrain/exposure, topography, direction history, duration, array zone, and windborne-debris context are load-bearing tropical-cyclone wind descriptors. | source_interpretation | TCWS-S001;TCWS-S004;TCWS-S005;TCWS-S006;TCWS-S010;TCWS-S012 | NHC definition; St. Croix mechanisms; design and experimental source scopes | T2_public_lab_standard_or_physics | event_to_local_demand_fields | adopt | Require or preserve the descriptors in a future bridge and keep unsupported effects explicit. | Collapse the descriptors to storm category or apply universal modifiers. | The source evidence changes demand and failure mechanisms with site, direction, duration, row, geometry, and debris conditions without calibrating one transferable modifier. | A validated reduced-order TC demand model supersedes individual fields.
TCWS-C005 | tropical_cyclone_wind | Ground-mounted fixed-tilt and single-axis-tracker arrays require separate architecture routes. | source_interpretation | TCWS-S005;TCWS-S006;TCWS-S007;TCWS-S010;TCWS-S011;TCWS-S012 | ASCE fixed-tilt provisions; FM §§2.1.2.1–2.1.2.4; tracker qualification and aeroelastic studies | T2_public_lab_standard_or_physics | array_architecture_selector | adopt | Require an explicit architecture and develop architecture-specific demand and failure-unit evidence. | Use one generic ground-mount curve or transfer fixed-tilt coefficients, tracker Ucrit, or stow behavior across architectures. | Rigid pressure response and tracker aeroelastic/control behavior are distinct mechanisms. | A formal equivalence study supports a shared record.
TCWS-C006 | tropical_cyclone_wind | Ceferino et al. analyze 14 large Caribbean ground-mounted sites and define extensive failure as clip or racking failure in more than 50 percent of panels. | direct_observation | TCWS-S002 | §2.1 and Table 1 pp. 2–3; Eq. 1 and §3.1 p. 4 | T1_claims_or_field_calibrated | ceferino_source_native_endpoint | adopt_audit_only | Describe and reproduce the source-native site-level extensive-structural-failure probability candidate. | Call the endpoint module DR, rack DR, whole-site DR, total loss, or repair-cost ratio. | The paper's atom and endpoint are a composite site limit state, not a failure-unit economic consequence. | Authors release a failure-unit disposition and same-unit cost crosswalk.
TCWS-C007 | tropical_cyclone_wind | Five of the 14 Ceferino ground-mounted sites had significant failure; failures began at reconstructed gusts near 83 m/s and the mean reconstructed gust among failed sites was about 91 m/s. | direct_observation | TCWS-S002 | §2.1 pp. 2–3 and §2.2 pp. 3–4 | T1_claims_or_field_calibrated | ceferino_field_observations | adopt_audit_only | Use as a small-sample source-native consistency check. | Treat 83 m/s as a universal onset or 91 m/s as a capacity threshold. | The observations are sparse, site-composite, and based on reconstructed rather than instrumented local gusts. | A larger architecture-labeled field dataset with local demand becomes available.
TCWS-C008 | tropical_cyclone_wind | Ceferino's ground-mounted posterior summaries have median v about 90 m/s and median beta about 0.15; reported posterior standard deviations are about 6 m/s and 0.07, and the mean posterior fragility rises from 10 to 90 percent over about 73 to 116 m/s. | direct_observation | TCWS-S002 | §4.2 and Figs. 5c/5d/6b p. 7 | T1_claims_or_field_calibrated | ceferino_posterior_candidate | defer_candidate_only | Preserve the summaries in the numerical candidate audit on the paper's reconstructed 3-second-gust axis. | Promote the numbers into a runtime DR curve, reinterpret beta as economic severity spread, or transfer them to a named fixed-tilt or tracker design. | The posterior characterizes site-level extensive structural failure probability for the source population only. | A transfer-qualified failure-unit and consequence bridge passes review.
TCWS-C009 | tropical_cyclone_wind | A deterministic lognormal curve built from Ceferino's posterior medians is not the paper's posterior-mean fragility curve. | source_interpretation | TCWS-S002 | Bayesian method and §4.2 posterior integration | T1_claims_or_field_calibrated | posterior_uncertainty_rule | adopt | Retain posterior uncertainty and distinguish parameter-summary diagnostics from posterior integration. | Label a median-parameter plug-in curve as the published posterior mean or ignore uncertainty from the 14-site sample. | The paper integrates fragility over posterior parameter samples; nonlinear averaging does not equal plugging in marginal medians. | Authors publish an authoritative deterministic reduction or full posterior artifact.
TCWS-C010 | tropical_cyclone_wind | Ceferino does not support a fixed-tilt-versus-tracker split or component-level curve decomposition. | source_interpretation | TCWS-S002 | Table 1 fields and §3.1 limit-state definition | T1_claims_or_field_calibrated | ceferino_transfer_limit | adopt | Keep the source candidate at generic large ground-mounted site grain. | Assign separate fixed-tilt, tracker, module, support, foundation, or electrical parameters from this study. | The reported site table lacks the architecture and component-disposition fields needed for those splits. | Architecture and component records for the 14 sites are released and validated.
TCWS-C011 | tropical_cyclone_wind | Ceferino's observed structural failures included cascading damage and debris from failed panels. | direct_observation | TCWS-S002 | §2.1 pp. 2–3 | T1_claims_or_field_calibrated | wind_and_debris_mechanism_boundary | adopt_with_limits | Preserve debris/cascade context when auditing the field fragility. | Call the candidate a clean aerodynamic-pressure-only response or separately price debris loss from the same observations. | The source-native observations combine mechanisms and do not identify their separate causal shares. | Matched event inspections isolate pressure, impact, and consequential damage.
TCWS-C012 | tropical_cyclone_wind | Perry et al. reviewed 1,534 mixed residential, commercial, and utility PV sites after Hurricanes Irma and Maria; 17 percent had visible damage and 2.8 percent had more than 50 percent visible damage. | direct_observation | TCWS-S003 | abstract p. 1012; §3.1 and Table 2 pp. 1016–1018 | T1_claims_or_field_calibrated | perry_remote_sensing_statistics | adopt_audit_only | Use as a broad field prevalence and imagery-method constraint. | Fit a utility-scale ground-mounted fragility or economic DR from the aggregate percentages. | The sample mixes asset classes and the reported endpoint is visible module-area damage, not a separately calibrated target-asset loss state. | The authors release a utility-scale ground-mounted subset with architecture, demand, inspection, and cost fields.
TCWS-C013 | tropical_cyclone_wind | Perry et al. found only a weak damage relationship with estimated maximum gust and documented strong installation/site heterogeneity. | direct_observation | TCWS-S003 | Figs. 4–5 pp. 1016–1018; Discussion pp. 1021–1022 | T1_claims_or_field_calibrated | installation_and_site_heterogeneity | adopt | Require mounting, installation, site, and local-demand descriptors in future field calibration. | Use gust alone as a sufficient universal predictor or infer a portable threshold from paired sites. | The field evidence shows materially different damage at nearby sites and identifies installation details as consequential but often proprietary. | A matched multivariate population dataset supports a reduced selector set.
TCWS-C014 | tropical_cyclone_wind | Perry's manual remote-sensing endpoint does not identify hidden electrical damage, component disposition, repair scope, or direct repair cost. | source_interpretation | TCWS-S003 | §2.4 pp. 1015–1016; Discussion pp. 1021–1022 | T1_claims_or_field_calibrated | remote_sensing_endpoint_limit | adopt | Use imagery for visible-damage screening and field-data design. | Convert percent module area missing or damaged into failure-unit economic DR. | Visible surface change is not a same-unit repair/replacement-cost endpoint and can miss internal or electrical damage. | Linked inspection, work-order, salvage, and cost records become available.
TCWS-C015 | tropical_cyclone_wind | The Ceferino and Perry evidence must not be counted as independent field populations without record-level deduplication. | governance_decision | TCWS-S002;TCWS-S003 | both studies' Caribbean Irma/Maria event and site descriptions | T1_claims_or_field_calibrated | evidence_dependence_rule | adopt | Treat them as complementary endpoint/method evidence with possible overlapping events and sites. | Multiply confidence or sample size as though the two sources were independent. | Both sources draw from the same regional hurricane seasons and public descriptions do not establish record-level independence. | Site identifiers establish overlap or independence.
TCWS-C016 | tropical_cyclone_wind | The DOE/FEMP St. Croix case documents a 469 kW fixed-tilt array assessed as total loss with rack, beam, clamp, fastener, corrosion, liberated-module, enclosure, conduit, inverter, switchgear, and transformer mechanisms. | direct_observation | TCWS-S004 | Executive Summary pp. vi–vii; §1.1/Table 1 pp. 2–3; §§2–3.6 pp. 5–12 | T3_engineering_proxy_or_adjacent_empirical | st_croix_mechanism_and_failure_unit_case | adopt_with_limits | Use the case to populate anatomy, dependency, inspection, and compound-peril fields. | Fit a population fragility, transfer the total-loss disposition, or infer component economic severities. | One detailed case exposes mechanisms but does not estimate a representative probability or cost-state distribution. | A population of comparable sites with local demands and itemized repair/replacement records is available.
TCWS-C017 | tropical_cyclone_wind | The St. Croix case combines high wind, wind-driven rain, and flash flooding; its reported approximately 104 mph event estimate and 145 mph design value are not population failure thresholds. | source_interpretation | TCWS-S004 | Executive Summary pp. vi–vii; §§1.1, 2, and 3 pp. 2–12 | T3_engineering_proxy_or_adjacent_empirical | compound_event_and_threshold_limit | adopt | Route pressure, debris, rain ingress, and flood mechanisms separately while preserving one parent event family. | Use either speed as a tropical-cyclone DR onset, design median, or evidence that the array failed below design solely from wind. | The case is compound and site specific; reported estimates do not isolate a wind-only causal threshold. | Forensic load reconstruction isolates mechanisms and component capacities.
TCWS-C018 | tropical_cyclone_wind | ASCE and fixed-tilt wind-tunnel evidence are design and demand anchors, not failure probability or economic severity evidence. | source_interpretation | TCWS-S005;TCWS-S010 | ASCE Chs. 26, 29, and 31; Browne abstract and §§1–5 | T2_public_lab_standard_or_physics | fixed_tilt_demand_bridge_boundary | adopt | Use exact edition, geometry, zone, exposure, and small-deflection eligibility in a future fixed-tilt local-demand bridge. | Treat code wind, design pressure, or a wind coefficient as as-built capacity, D50, damage state, or DR. | Design adequacy calculations and load coefficients do not measure population failure disposition or repair cost. | Matched component demand-capacity-failure-cost evidence passes review.
TCWS-C019 | tropical_cyclone_wind | Tracker critical velocity is exact-system, angle, layout, direction, row, and qualification dependent. | source_interpretation | TCWS-S006;TCWS-S007;TCWS-S011;TCWS-S012 | FM §§2.1.2.3–2.1.2.4; IEC scope; aeroelastic benchmark and stability-map results | T2_public_lab_standard_or_physics | tracker_ucrit_and_state_contract | adopt | Require exact tracker system, qualification, configuration, attained angle, drive/lock state, position, direction, and compatible speed basis before using Ucrit. | Supply a generic Ucrit, infer it from IEC qualification, or transfer benchmark critical speed to an unnamed production tracker or TC field. | The studies show instability depends on the defined system and state; qualification identity is necessary but does not itself supply a generic value. | A governed certified tracker-capacity catalog with structured equivalence becomes available.
TCWS-C020 | tropical_cyclone_wind | FM's trigger at 25 percent below tested instability speed is an operational action margin, not damage onset. | source_interpretation | TCWS-S006 | §§2.1.2.3–2.1.2.4 pp. 3–4 | T2_public_lab_standard_or_physics | tracker_stow_action_gate | adopt_flag_only | Use 0.75 Ucrit only as an exact-basis control/action flag after all qualification fields match. | Force positive damage at the trigger, force zero below it, calibrate a fragility median from it, or apply it across mismatched speed definitions. | The source specifies an operating margin below tested instability, not an observed failure threshold. | FM changes the criterion or matched damage observations calibrate the relationship.
TCWS-C021 | tropical_cyclone_wind | IEC 62817 tracker qualification and IEC 61730 module safety qualification are selector provenance, not tropical-cyclone fragility. | source_interpretation | TCWS-S007;TCWS-S008 | official IEC scope and test-purpose pages | T2_public_lab_standard_or_physics | qualification_provenance_rule | adopt | Record the exact standard, edition, product, configuration, and test identity. | Infer site wind capacity, TC survival, failure probability, economic severity, or mitigation credit from qualification alone. | Qualification standards define test and safety scope but do not provide the target population's hazard-to-cost response. | A product-specific qualified capacity and field-validation artifact is authorized.
TCWS-C022 | all_shared | The NLR Q1-2025 UPV benchmark is a reference value source only, under value_source_id NLR_Q1_2025_UPV_PV_ONLY_2024_USD. | value_rule | TCWS-S013 | dataset landing page and governed parent value ledger | T2_public_lab_standard_or_physics | reference_value_lineage | adopt_with_limits | Use exact row-level units, vintage, and denominator mapping after the parent-ledger crosswalk is verified. | Use benchmark shares as damage caps, exposed fractions, site appraisal, support-allocation rules, or failure severity. | Cost structure can support a denominator but supplies no hazard response or repair disposition. | A new benchmark vintage or site-specific BOM/value ledger supersedes the reference.
TCWS-C023 | tropical_cyclone_wind | PV_GSU_SUBSTATION remains a separate solar-plant failure unit and is withheld, not assigned zero and not inherited from a generic hurricane substation placeholder. | governance_decision | TCWS-S004;TCWS-S013;LEG-TCWS-001;LEG-TCWS-002;GOVERNANCE_CONTRACT | St. Croix electrical mechanisms; value lineage; legacy substation rows; coverage gate | T4_placeholder_or_expert_judgment | PV_GSU_SUBSTATION_coverage | historical_scope_only | Preserve point or yard exposure, component value, and separate future evidence routing. | Apply whole-array exposure, legacy substation logistic DR, flood/rain loss, or zero immunity to the GSU. | A shared GSU has different spatial grain, mechanisms, values, and evidence needs from the array field. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | GSU-specific TC wind demand, disposition, exposure, and same-unit cost data pass review.
TCWS-C024 | tropical_cyclone_wind | PV_POWER_CONVERSION_AND_COLLECTION remains a separate withheld unit for inverters, combiners, wiring, enclosures, collection, grounding, and related power-path equipment. | governance_decision | TCWS-S004;TCWS-S009;TCWS-S013;GOVERNANCE_CONTRACT | St. Croix §§3.4–3.6; Owner's Guide §5; value and coverage audits | T3_engineering_proxy_or_adjacent_empirical | PV_POWER_CONVERSION_AND_COLLECTION_coverage | historical_scope_only | Keep the equipment anatomy and value/exposure seam explicit for later evidence. | Scale it by array structural DR, call it wind immune, or mix wind-driven rain/flood ingress into a wind-only curve. | The unit has different direct and dependency mechanisms and lacks a matched wind-to-disposition-to-cost chain. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | Unit-specific demand, disposition, repair, and cost evidence becomes available.
TCWS-C025 | tropical_cyclone_wind | The strong_wind_solar package may contribute source discovery, anatomy, terminology, and governance controls but no numeric transfer. | governance_decision | TCWS-S015;GOVERNANCE_CONTRACT | cross-cell register rows and neighboring-wind boundary | T3_engineering_proxy_or_adjacent_empirical | cross_cell_reuse_rule | historical_scope_only | Reuse reviewed primary-source lineage after independent registration and pathway-specific transfer analysis. | Inherit convective demand axes, downburst profiles, curve forms, T4 medians, beta, severity, stow credit, or exposure behavior. | Asset substrate is reusable, while causal wind fields and numeric evidence are pathway specific. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C001/005/006; the underlying evidence limitation is retained. | A formal numerical equivalence review passes.
TCWS-C026 | tropical_cyclone_wind | The legacy hurricane-solar memo mischaracterizes Ceferino's ground-mounted result and its logistic parameters are rejected for runtime. | legacy_audit_finding | TCWS-S002;LEG-TCWS-001 | Ceferino §4.2 p. 7; legacy memo §§2.6–2.8, §5, Appendix A; index rows 219–299 | T4_placeholder_or_expert_judgment | legacy_curve_bundle | reject_runtime_retain_audit | Preserve exact numbers for source correction, migration reproduction, and regression tests only. | Adopt architecture shifts, caps, slopes, midpoints, confidence labels, or an economic interpretation from the memo. | The legacy record substitutes 58 m/s and beta 0.30 for the paper's roughly 90 m/s and 0.15 ground posterior, then adds unsupported architecture and severity assumptions. | A separately calibrated, fully provenance-resolved curve passes promotion gates.
TCWS-C027 | tropical_cyclone_wind | Hazard Modeling's provisional hurricane-solar implementation is a migration fixture only. | legacy_audit_finding | LEG-TCWS-002;GOVERNANCE_CONTRACT | 01_damage.py lines 14–39, 56–105, 136–183, 197–207 | T4_placeholder_or_expert_judgment | legacy_consumer_behavior | reject_runtime_retain_audit | Reproduce exact old behavior for cutover comparison. | Treat hardcoded PV, mounting, substation, or zero-remainder TIV weights and anchored logistics as calibrated Damage outputs or a valid fallback. | The consumer mixes mechanisms and unsupported value shares and labels absent coverage as approximately immune. | A governed promoted Damage artifact and explicit consumer cutover replace the fixture.
TCWS-C028 | tropical_cyclone_wind | No public matched chain was located in the bounded review from representative local tropical-cyclone demand through failure-unit state and disposition to same-unit direct repair or replacement cost. | governance_decision | TCWS-S002;TCWS-S003;TCWS-S004;BOUNDED_SEARCH_LOG | bounded-search chain matrix and endpoint pressure tests | T3_engineering_proxy_or_adjacent_empirical | runtime_curve_gate | withhold | Use the bounded result as the reason for NO_RUNTIME_CURVE and as an evidence-acquisition roadmap. | Claim universal absence across private owner, OEM, insurer, non-indexed, non-English, or post-cutoff evidence. | Strong sources stop at site probability, visible damage, design/demand, qualification, or a compound single-site case. | Authorized matched event, configuration, inspection, disposition, and cost records close the chain.
TCWS-C029 | tropical_cyclone_wind | Wind, debris impact, wind-driven rain, flood or surge, and TC-spawned tornado pathways preserve one event_family_id but route separately. | governance_decision | TCWS-S004;GOVERNANCE_CONTRACT | St. Croix compound-event evidence; event-identity and neighboring-hazard controls | T4_placeholder_or_expert_judgment | compound_event_identity_rule | adopt | Coordinate one physical occurrence and downstream loss assembly without duplicate value consumption. | Blend all mechanisms into a wind curve or count one damaged value stock independently in several pathways. | The same cyclone can produce distinct mechanisms whose evidence and exposure grains differ. | A governed multi-pathway consequence assembler supersedes the current rule.
TCWS-C030 | tropical_cyclone_wind | Model v0.1/docs r1 is a noncanonical coverage scaffold with zero runtime curve records; scalar damage and monetary loss are withheld. | governance_decision | GOVERNANCE_CONTRACT | change classification, capability declaration, and fail-closed release gate | T4_placeholder_or_expert_judgment | canonical_runtime_artifact=false; curve_records=[] | historical_scope_only | Return null with stable reason code NO_RUNTIME_CURVE after identity and input validation. | Return zero, a site fragility probability, a legacy proxy, or an adjacent-cell fallback as DR or loss. | No candidate completes the physical-state, economic-severity, exposure, and provenance chain required for runtime publication. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | A governed model v1.0 behavior change passes evidence, seven-step, tests, schemas, capability, and release review.
TCWS-C101 | tropical_cyclone_wind | The Perry manual dataset contains 47 records, including 37 ground-mounted and 35 ground-mounted records explicitly marked tracking false. | direct_observation | TCWS-S020 | manual CSV filter counts pinned to source SHA | T1_claims_or_field_calibrated | source_cohort_count | adopt | Freeze the exact source-cohort selection. | Call all 35 records utility-scale or representative of a named modern fleet. | System size is missing for part of the cohort and the source does not declare one target utility archetype. | A licensed revised source file or corrected schema changes the counts.
TCWS-C102 | tropical_cyclone_wind | The manual endpoint is percent modules visibly damaged based on post-event imagery and labeled site/damage polygons. | direct_observation | TCWS-S003;TCWS-S020;TCWS-S021 | paper method and data-description pp. 1-2 | T1_claims_or_field_calibrated | source_response_endpoint | adopt_with_limits | Use the visible module fraction as a graded physical response. | Infer hidden electrical or structural damage, disposition, labor, or whole-site cost. | Remote sensing observes exterior visible damage only. | A source revision adds inspected disposition and same-unit cost.
TCWS-C103 | tropical_cyclone_wind | Under uniform per-module hardware value and full replacement of every visible or missing module, visible module fraction equals a same-unit module-hardware material replacement proxy DR. | governance_assumption | TCWS-S020;TCWS-S021;GOVERNANCE_CONTRACT | v1 ordinate bridge derivation | T4_placeholder_or_expert_judgment | uniform_value_and_full_replacement_bridge | adopt_with_limits | Emit a source-specific module-hardware screening DR only when both assumptions are explicitly acknowledged. | Describe the result as observed economic loss, claims-calibrated DR, installed replacement cost, or full module-field all-damage DR. | The physical numerator and denominator align only because the two economic bridge assumptions are imposed. | Disposition or module-level value evidence replaces either assumption.
TCWS-C104 | tropical_cyclone_wind | The source x field is the dataset-reported event maximum gust in m/s; provider, station, height, averaging period, exposure, and query semantics are not pinned for the full manual multi-hurricane cohort. | direct_observation | TCWS-S020;TCWS-S021 | manual CSV max_wind_gust_(m/s) and data-description weather notes | T1_claims_or_field_calibrated | hazard_axis | adopt_with_limits | Require the exact dataset-reported axis identifier. | Alias NHC sustained wind, ASCE 3-second gust, array-height wind, Visual Crossing generally, or another gust product. | A numeric gust without complete source semantics is not universally transferable. | The archive publishes exact full-cohort weather-query semantics or an approved bridge is validated.
TCWS-C105 | tropical_cyclone_wind | The runtime fit uses 34 source-cohort records from 17.4 through 39.1 m/s. | derived_result | TCWS-S020;GOVERNANCE_CONTRACT | ground and tracking=false; x<=39.1 filter | T3_engineering_proxy_or_adjacent_empirical | fit_population_and_range | adopt | Evaluate only inside the governed source-bounded range. | Extrapolate below 17.4 or above 39.1 m/s. | The next observed point is a lone severe-tail record separated by a 9.1 m/s gap. | A sufficiently populated tail dataset supports a revised range.
TCWS-C106 | tropical_cyclone_wind | The one 48.2 m/s source-cohort record has visible damage fraction 0.4142383192 and is audit-only. | direct_observation | TCWS-S020 | manual CSV source cohort sparse-tail record | T1_claims_or_field_calibrated | sparse_tail_audit | withhold_runtime | Retain the point in evidence QA and tail-influence discussion. | Use it as a runtime knot or interpolate the 39.1-48.2 m/s gap. | One clustered observation cannot stabilize the severe tail. | Additional architecture-matched observations close the gap and tail.
TCWS-C107 | tropical_cyclone_wind | The runtime curve is an unweighted site-level monotone PAVA fit linearized at pooled-block edges. | method_decision | TCWS-S020;GOVERNANCE_CONTRACT | FIT_SUFFICIENT_STATISTICS and derivation script | T3_engineering_proxy_or_adjacent_empirical | fit_method | historical_scope_only | Reproduce deterministic nondecreasing block means and linear interpolation between recorded edges. | Claim a source-published curve, iid confidence interval, claims calibration, or causal parametric fragility. | Site weighting avoids inventing module counts; monotonic pooling is transparent for sparse zero-inflated observations. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS-C220; the underlying evidence limitation is retained. | A reviewed cluster-aware predictive method supersedes the screening fit.
TCWS-C108 | tropical_cyclone_wind | No curve-intrinsic uncertainty distribution is carried. | governance_decision | TCWS-S020;GOVERNANCE_CONTRACT | FIT_EVENT_SENSITIVITY_tropical_cyclone_wind_solar__model_v1_0__docs_r1.csv | T4_placeholder_or_expert_judgment | uncertainty_status | withhold | Flag event clustering and fit sensitivity. | Treat row count as iid evidence or construct unsupported confidence bands. | Events and sites are clustered; leave-Maria-out reduces the highest fitted block by about 5.41 times and the severe tail is sparse. | A hierarchical event-aware uncertainty model passes review.
TCWS-C109 | tropical_cyclone_wind | The observed site fraction already contains realized spatial extent and must not be multiplied by a second array exposure fraction. | governance_decision | TCWS-S003;TCWS-S020;TCWS-S021 | source endpoint definition | T3_engineering_proxy_or_adjacent_empirical | exposure_rule | adopt | Apply the DR once to the exact compatible module-hardware subject value. | Apply an additional at-risk fraction or site overlap multiplier to the same response. | A second fraction would double-attenuate the observed response. | A future local-demand model changes the response grain.
TCWS-C110 | tropical_cyclone_wind | The source does not isolate pure aerodynamic uplift from cascade or debris-related visible module loss. | source_interpretation | TCWS-S003;TCWS-S020;TCWS-S021 | paper discussion and dataset fields | T3_engineering_proxy_or_adjacent_empirical | causal_scope_acknowledgement | adopt_with_limits | Label output SOURCE_COMPOSITE_HURRICANE_MODULE_LOSS. | Present the proxy as pure wind-pressure fragility or combine it with a debris module curve without overlap review. | Post-event imagery does not identify the causal mechanism of each damaged module. | Mechanism-labeled event observations become available.
TCWS-C111 | tropical_cyclone_wind | Tracker modules and tracker SBOS are unsupported by this curve. | governance_decision | TCWS-S006;TCWS-S020 | manual cohort has only two ground tracking=true records | T2_public_lab_standard_or_physics | architecture_selector | historical_scope_only | Route tracking=false source-cohort screening only. | Fallback from tracker to fixed tilt or infer stow benefit. | Two tracker records cannot support a tracker route and tracker controls change response. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C005/009; the underlying evidence limitation is retained. | A qualified tracker dataset passes the full evidence chain.
TCWS-C112 | tropical_cyclone_wind | Racking, foundations, power conversion, collection, GSU, SCADA, civil, fieldwork, logistics, and hidden damage remain withheld rather than zero. | governance_decision | TCWS-S003;TCWS-S006;TCWS-S020;GOVERNANCE_CONTRACT | failure-unit coverage audit | T4_placeholder_or_expert_judgment | partial_coverage | historical_scope_only | Emit explicit null results and reason codes. | Transfer the module proxy, assume zero loss, or multiply by plant TIV. | The source endpoint and value bridge cover visible module hardware only. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | Failure-unit-specific evidence and value chains pass review.
TCWS-C113 | tropical_cyclone_wind | Scenario dollar loss and all annual or tail metrics are withheld before canonical promotion. | governance_decision | TCWS-S013;GOVERNANCE_CONTRACT | capability and value-linkage gate | T4_placeholder_or_expert_judgment | loss_capability | historical_scope_only | Review scalar source-unit DR independently of financial output. | Use the NLR benchmark, full TIV, EAL, PML, VaR, or TVaR from this proposal. | The proposal is noncanonical and has partial physical and value coverage. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | Canonical promotion plus exact site module-hardware value and consumer validation.
TCWS-C114 | tropical_cyclone_wind | Raw DOI files are hash-pinned but not redistributed in-repository because the archive metadata reports no license. | governance_decision | TCWS-S020;TCWS-S021 | DOI resource metadata and pinned file hashes | T4_placeholder_or_expert_judgment | source_file_handling | adopt | Publish sufficient statistics and a reproducible derivation script that requires a user-supplied DOI download. | Commit the raw CSV or PDF as if reuse permission were granted. | A public download is not the same as an explicit redistribution license. | The archive supplies a compatible license or written permission.
TCWS-C115 | tropical_cyclone_wind | Ceferino Supplementary Table 2 and Perry report materially different damage percentages at four apparent coordinate-nearest Caribbean matches and must not be pooled as one measurement system. | cross_source_discrepancy | TCWS-S003;TCWS-S020;TCWS-S022 | CROSS_METHOD_MATCH_AUDIT_tropical_cyclone_wind_solar__model_v1_0__docs_r1.csv; Ceferino Supplementary Table 2 p. 4; Perry aggregate CSV lines 7, 74, 242, 257 | T3_engineering_proxy_or_adjacent_empirical | cross_method_same_event_endpoint_challenge | adopt_as_limitation | Treat the disagreement as correlated cross-method evidence of measurement and endpoint uncertainty and block canonical promotion. | Average, pool, treat the values as independent labels, assert an authoritative identity join, or use Ceferino/Perry aggregate values in the Perry manual-cohort PAVA fit. | The analyst-derived nearest-coordinate rule finds four same-event utility/ground records within 500 m, but no authoritative shared site identifier adjudicates identity; the sources use different labeling methods and do not establish one common endpoint. | A reconciled site-level adjudication establishes shared identity and common endpoint semantics.
TCWS-C116 | tropical_cyclone_wind | Under the strict evidence-earned economic-DR gate, current evidence supports a docs-only v0.1 update rather than a numerical model v1. | independent_review_finding | TCWS-S020;TCWS-S021;TCWS-S022;GOVERNANCE_CONTRACT | independent primary-source and repo audits dated 2026-07-29 | T4_placeholder_or_expert_judgment | strict_gate_outcome | adopt_as_limitation | Label model v1 as a deliberate coverage-first noncanonical screening exception only. | Describe model v1 as evidence-earned, canonical, field-calibrated economic DR, or ready for Hazard cutover. | The T4 ordinate bridge, population transfer, source-axis ambiguity, endpoint conflict, clustering, and sparse tail remain unresolved. | All strict promotion gates pass.
TCWS-C117 | tropical_cyclone_wind | The released manual CSV has 47 rows and omits the paper-described site_type field, so the governed cohort follows the released file rather than the paper's narrative count/schema. | source_release_discrepancy | TCWS-S003;TCWS-S020 | paper Methods/Data Availability compared with manual CSV header and row count | T1_claims_or_field_calibrated | source_release_schema_qa | adopt_as_limitation | Pin 47 rows, the released columns, and the exact SHA for reproducibility. | Silently assume a 48th row, infer site type from missing fields, or call the 35-row cohort utility-scale. | The public artifact and narrative do not fully align; the released file is the reproducible numerical object. | Authors publish a corrected/versioned data release and change log.
TCWS-C118 | tropical_cyclone_wind | Ceferino's paper defines extensive failure using a strict greater-than-50-percent threshold, but Supplementary Table 2 contains one site at exactly 50 percent: the table yields 4/14 under greater-than 50 percent, while the reported 36 percent corresponds to 5/14 only when 50 percent is included. | source_internal_threshold_discrepancy | TCWS-S002;TCWS-S022 | paper Section 2.1 and Supplementary Table 2 p. 4 | T1_claims_or_field_calibrated | ceferino_binary_endpoint_reproduction | adopt_as_limitation | Retain the discrepancy as a governed endpoint-semantics warning and do not independently reproduce the binary calibration count from the supplement. | Silently classify the 50-percent row, claim that the supplement exactly reproduces the reported binary sample, or use either count in the Perry fit. | The strict textual threshold and the reported proportion cannot both be reproduced from the tabulated percentages without an inclusion convention or author clarification. | Authors publish a corrected threshold, exact binary labels, or a site-level calibration table.
TCWS-C201 | tropical_cyclone_wind | Perry identifies Visual Crossing API as the study-level hurricane maximum-gust provider, while the released row-level station, product, query, duration, height, exposure, retrieval-version, time-of-maximum, and uncertainty lineage remains unresolved. | source_semantics_correction | TCWS-S003;TCWS-S020;TCWS-S023;TCWS-S024 | Perry Figure 3 journal p. 1015; released manual CSV schema; Visual Crossing wind and historical-construction documentation | T3_engineering_proxy_or_adjacent_empirical | perry_axis_provider_wording | adopt | State Visual Crossing as study-level provider and retain the exact Perry source-axis label. | Call the Perry field measured at site, exact 3-second, ASCE Exposure C, reproducible from today's API, or a single station/grid product. | Provider identity does not recover the discarded row-level query and reference-frame lineage. | Archived author request/response records and station contributors are released.
TCWS-C202 | tropical_cyclone_wind | No portable identity or fixed-factor bridge is supported between Hazard's modeled 3-second gust object and the Perry dataset-reported event maximum gust. | axis_bridge_decision | TCWS-S003;TCWS-S005;TCWS-S020;TCWS-S023;TCWS-S024;GOVERNANCE_CONTRACT | axis audit dated 2026-07-29 and consumer handoff comparison | T4_placeholder_or_expert_judgment | hazard_to_perry_axis_bridge | withhold | Evaluate only the exact Perry field within the pinned source range. | Pass ordinary Hazard gust, NHC sustained wind, ASCE design wind, category, or another gust product directly into the curve. | Matching units cannot close duration, spatial, exposure, product, and query semantics. | A versioned paired reconstruction and held-out transfer validation pass review.
TCWS-C203 | tropical_cyclone_wind | Paper and released manual-data inconsistencies include 48 versus 47 sites, one Florence count difference, differing event-window end dates, and a combined Irma/Maria narrative whose manual rows are Maria-labeled with a Maria-only window. | source_release_discrepancy | TCWS-S003;TCWS-S020 | paper Methods and Figures 3-5 compared with pinned manual CSV | T1_claims_or_field_calibrated | event_window_lineage_qa | adopt_as_limitation | Use the pinned released CSV and record the attribution uncertainty. | Silently reconstruct a missing row, relabel events, or infer portable event-window gust semantics. | The numerical file is reproducible but not fully identical to the paper narrative. | Authors publish a corrected versioned release and change log.
TCWS-C204 | tropical_cyclone_wind | Typhoon Mawar ground fixed-tilt observations provide a severe-event audit but do not support a Perry tail fit or a generic gust-only solar curve. | external_severe_audit | TCWS-S025 | report pp. 9-12 and Figure A-2 p. 78 | T3_engineering_proxy_or_adjacent_empirical | severe_tail_external_audit | adopt_as_limitation | Use near-zero visible ground-module loss under severe estimated winds as a transfer challenge. | Pool Mawar with Perry or infer tail shape, economic DR, or immunity. | Wind, architecture, installation quality, response endpoint, and measurement basis are not compatible with the Perry atom. | Architecture-matched raw data and a qualified common wind axis become available.
TCWS-C205 | tropical_cyclone_wind | Mawar's report contains conflicting ground-module damage counts and some inconsistent site wind summaries, so its rows remain audit-only pending clarification. | source_internal_discrepancy | TCWS-S025 | Table 1, Table 7, Figure A-2, and Dandan detailed assessment | T1_claims_or_field_calibrated | mawar_numerical_ingestion_gate | withhold | Retain qualitative and bounded audit conclusions. | Serialize one conflicting count or wind estimate as a governed curve record. | A numerical atom must have one adjudicated numerator, denominator, and demand record. | Authors or repository publish corrected machine-readable data.
TCWS-C206 | tropical_cyclone_wind | Typhoon Yagi's regional satellite-area loss and generic unit-area cost are not compatible with the Perry failure unit or the repository economic DR ordinate. | cross_source_endpoint_decision | TCWS-S026;TCWS-S027 | Methods Sections 2.1.2, 2.2.3-2.2.4, Eq. 8, results, and limitations | T3_engineering_proxy_or_adjacent_empirical | yagi_transfer_rule | audit_only | Use as a regional event-scale external screen and acquisition lesson. | Transfer wind-scale coefficients, area loss, or generic costs to module, rack, plant, or same-unit DR. | Architecture and component disposition are unknown and the cost is not observed same-unit repair cost. | Architecture-resolved inspection and cost/value records are released.
TCWS-C207 | tropical_cyclone_wind | Current evidence does not support a tracker route, fixed-to-tracker fallback, or generic stow credit. | architecture_release_decision | TCWS-S006;TCWS-S020;TCWS-S025;TCWS-S038;TCWS-S039 | Perry tracker count; Mawar tracker section; OEM cases | T4_placeholder_or_expert_judgment | tracker_route_status | historical_scope_only | Capture tracker identity and command/attained state for future evidence. | Use the fixed Perry curve for trackers or emit favorable response from a commanded stow state. | Two Perry rows, zero Mawar trackers, and incomplete OEM cases cannot define response or cost. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C001/009/010; the underlying evidence limitation is retained. | A multi-event tracker cohort closes demand, attained state, inspection, disposition, and economics.
TCWS-C208 | tropical_cyclone_wind | FPL's reported fleet panel damage or replacement fractions are censored occurrence-count observations, not economic damage ratios or site fragility points. | field_occurrence_boundary | TCWS-S028;TCWS-S030;TCWS-S031 | FPL Jarro Ian and Milton testimony and Helene/Milton testimony | T1_claims_or_field_calibrated | fleet_panel_fraction_use | adopt_with_limits | Use the stated bounds for external validation and data-request design. | Treat them as site DR, pair them to an assumed gust, or multiply them by module or plant value. | The reports omit a common exposed-site denominator, local intensity, architecture, and same-unit cost/value. | Event/site/component records with exact denominators and wind are supplied.
TCWS-C209 | tropical_cyclone_wind | Regulatory restoration schedules show that contractor, logistics, labor, material, vehicle, inspection, and civil scopes can be material and must be separated and allocated once. | cost_scope_boundary | TCWS-S028;TCWS-S029;TCWS-S030 | FPL restoration testimony and cost exhibits | T3_engineering_proxy_or_adjacent_empirical | support_allocation_rule | adopt | Design work-order ingestion and once-only support allocation. | Use mixed generation cost shares as solar vulnerability, failure-unit DR, or default support multipliers. | The cost buckets span preparation, restoration, logistics, inspection, civil work, and multiple facilities. | Failure-unit-linked work orders and an approved allocation ledger become available.
TCWS-C210 | tropical_cyclone_wind | FEMA field cases support architecture-specific module, post, purlin, connector, and rack physical states but not same-unit economic DR. | physical_occurrence_evidence | TCWS-S032 | USVI MAT Sections 7.1.2-7.1.3 | T1_claims_or_field_calibrated | fixed_structure_occurrence_use | adopt_with_limits | Use physical counts and mechanisms for failure-unit and inspection design. | Convert affected fractions or qualitative facility damage directly to economic DR. | Repair disposition, invoices, salvage, and matching replacement value are absent. | Owner/adjuster cost and value schedules join to the inspected units.
TCWS-C211 | tropical_cyclone_wind | Owner records document removal, redesign, limited repair, and electrical replacement outcomes, but redesign and compound electrical damage prevent like-kind wind DR calibration. | owner_disposition_evidence | TCWS-S033;TCWS-S034 | BMR project Context and Process sections | T1_claims_or_field_calibrated | terminal_disposition_context | adopt_with_limits | Use as categorical disposition and selector/compound-pathway evidence. | Treat redesigned replacement cost, moisture/static electrical work, or facility removal as transferable wind-only DR. | The outcome scope is broader or different from like-kind direct physical repair of one declared unit. | Itemized same-unit work orders and pre-event replacement values are released.
TCWS-C212 | tropical_cyclone_wind | Plant-level SEC loss estimates and availability statements are materiality evidence but prohibited economic-DR numerators. | economic_scope_boundary | TCWS-S035 | AES 2017 Q3 Form 10-Q specified lines | T1_claims_or_field_calibrated | plant_loss_estimate_use | audit_only | Use to establish that physical and nonphysical scopes require explicit separation. | Divide loss by MW, unavailable capacity, historic capex, or assumed value and call the result DR. | Reported loss can include property, business interruption, cleanup, recovery, or other scope and lacks same-unit value. | Audited direct physical cost and event-date replacement value are disclosed separately.
TCWS-C213 | tropical_cyclone_wind | DOE/FEMP forensic cases extend physical coverage to modules, racks, conduit, inverters, switchgear, transformers, and compound water pathways without closing numerical economic response. | multi_failure_unit_evidence | TCWS-S036 | in-person assessment and failure analysis PDF pp. 9-15 | T1_claims_or_field_calibrated | secondary_failure_unit_status | adopt_with_limits | Improve the unit inventory, pathway split, and acquisition plan. | Convert total-loss wording or estimated site wind into component or whole-site economic DR. | The case mixes wind, rain, flood, and design/installation weaknesses and lacks same-unit cost/value. | Pathway-separated component work orders and values are supplied.
TCWS-C214 | tropical_cyclone_wind | NLR/NREL BOM and hardening-cost evidence supports value anatomy and selectors only, not occurrence vulnerability or repair savings. | value_method_boundary | TCWS-S013;TCWS-S037 | Q1-2025 value source and NREL severe-weather Tables 1-2 | T2_public_lab_standard_or_physics | benchmark_value_use | adopt_with_limits | Reconcile physical value buckets and define data-request fields. | Use benchmark weights or hardening premiums as damage probabilities, DRs, reinstatement values, or mitigation credits. | New-build anatomy and prospective premiums do not observe event damage consequence. | Site-specific event-date replacement values and outcome data are provided.
TCWS-C215 | tropical_cyclone_wind | Every generic fixed, tracker, support-structure, foundation, electrical, GSU, SCADA, civil, and support numerical route remains withheld in docs r2. | coverage_release_decision | TCWS-S025;TCWS-S028;TCWS-S030;TCWS-S032;TCWS-S036;TCWS-S040;GOVERNANCE_CONTRACT | docs-r2 failure-unit gap matrix | T4_placeholder_or_expert_judgment | expanded_failure_unit_release_status | historical_scope_only | Use the evidence to improve coverage documentation and acquisition requirements. | Infer zero damage, borrow the Perry module screen, or blend cross-source physical fractions and costs. | No reviewed source closes the complete target chain for any additional atom. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C001/005/012/013; the underlying evidence limitation is retained. | A failure-unit-specific evidence package passes every promotion gate.
TCWS-C216 | tropical_cyclone_wind | Strong-wind solar work is reusable for anatomy, demand framing, selectors, value ledgers, dependency rules, evaluators, and KAT structure, but not for numerical tropical-cyclone response. | cross_cell_reuse_decision | GOVERNANCE_CONTRACT | docs-r2 reuse blueprint and neighboring strong_wind_solar package | T4_placeholder_or_expert_judgment | strong_wind_reuse_scope | historical_scope_only | Reuse structure and controls with tropical-cyclone-specific evidence. | Copy convective knots, coefficients, state credits, or tail behavior into the TC cell. | Duration, direction history, rain, debris, cycling, and compound pathways differ. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C005/006; the underlying evidence limitation is retained. | A qualified cross-hazard transfer study passes independent review.
TCWS-C217 | tropical_cyclone_wind | The deep-curation result is an evidence-only docs-r2 revision; model v1.1 and model v2.0 are not earned and docs-r1 runtime behavior remains unchanged. | versioning_decision | TCWS-S020;TCWS-S023;TCWS-S025;TCWS-S028;TCWS-S032;TCWS-S036;GOVERNANCE_CONTRACT | change classification and deep-curation decision dated 2026-07-29 | T4_placeholder_or_expert_judgment | version_action | historical_scope_only | Retain model v1.0 as a noncanonical exact-source screening atom and model v0.1 as strict fail-closed alternative. | Change knots, range, axis, selectors, outputs, package, index, or consumer pin under a docs-only label. | New evidence sharpens limitations and design but supplies no adopted numerical parameter. Consolidated v2 register: prior-version conclusion is scoped/superseded by TCWS2-C001/002; the underlying evidence limitation is retained. | An output-bearing evidence package passes review and is classified separately.
TCWS-C218 | tropical_cyclone_wind | The minimum v2 package requires portable local wind, exact architecture and attained state, affected and unaffected inspections, terminal disposition, same-unit direct cost and replacement value, separated support, and compound-pathway attribution. | acquisition_requirement | TCWS-S025;TCWS-S028;TCWS-S030;TCWS-S032;TCWS-S036;TCWS-S038;TCWS-S040;GOVERNANCE_CONTRACT | docs-r2 v2 acquisition blueprint | T4_placeholder_or_expert_judgment | v2_minimum_evidence_package | adopt | Use as acceptance criteria for owner, adjuster, OEM, or contractor data. | Promote a candidate merely because one field or one public case becomes available. | Every current blocker maps to a missing field or linkage in this package. | The package is acquired, validated, and independently reviewed.
TCWS-C219 | tropical_cyclone_wind | No interpolation, monotonicity, selector, range, or evaluator defect was identified in the existing Perry source-specific screening atom within its exact declared domain. | independent_review_finding | TCWS-S003;TCWS-S020;GOVERNANCE_CONTRACT | docs-r1 validator and docs-r2 independent review synthesis | T4_placeholder_or_expert_judgment | existing_curve_internal_status | adopt_with_limits | Retain the exact noncanonical research atom unchanged. | Describe it as general hurricane-solar, utility-scale, CONUS, tracker, whole-plant, dollar, or tail coverage. | The numerical implementation is coherent; its applicability is deliberately narrow and its strict economic-evidence gate remains NO-GO. | A reproducibility defect or changed source artifact is found.
TCWS-C220 | tropical_cyclone_wind | The Perry PAVA fit is equal-record weighted rather than strictly unique-site weighted because at least one physical site recurs across storm records. | source_cohort_dependence_finding | TCWS-S020 | manual CSV sites 7 and 14; coordinates, area, installation year, and event labels; docs-r2 independent source replay | T1_claims_or_field_calibrated | fit_weighting_interpretation | adopt_as_limitation | Describe each retained record as one vote and disclose repeated physical sites across events. | Claim 34 independent sites or interpret the historical EQUAL_SITE_WEIGHT_NOT_MODULE_WEIGHTED flag as proof of unique-site independence. | The implementation weights rows equally; physical-site and event dependence remain in the cohort. | A governed unique-site/event identifier and cluster-aware refit replace the current cohort.
TCWS-C221 | tropical_cyclone_wind | The pinned PAVA is a reproducible finite-sample descriptive smoother, but no scientifically validated predictive relationship is established even for an unseen source-compatible site. | predictive_validity_decision | TCWS-S003;TCWS-S020;GOVERNANCE_CONTRACT | manual convenience cohort, six-event cluster counts, leave-one-event sensitivity, repeated-site audit, and interpolation method | T4_placeholder_or_expert_judgment | predictive_use_status | withhold | Use the curve only for governed descriptive replay or explicitly experimental screening with all limitations. | Call it a validated predictive vulnerability relationship, population expectation, or calibrated response for a new site. | No sampling frame, selection model, independent validation event, cluster-aware inference, or controlled architecture/design adjustment exists; PAVA and block-edge interpolation impose shape. | Representative architecture-resolved event cohorts and event-held-out predictive validation pass review.
TCWS2-C001 | tropical_cyclone_wind | The requested v2 is a deliberate coverage-first synthetic Tier-4 exception, not an evidence-earned hurricane calibration. | governance_decision | GOVERNANCE_CONTRACT;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | DECISION_LOG model-v2 docs-r1 § TCWS2-D001 | T4_placeholder_or_expert_judgment | model_grade=experimental_synthetic_T4_scenario | adopt | Evaluate the proposal for bounded research and contract integration. | Describe any generic curve as empirical, calibrated, conservative, or production ready. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Formal elicitation or matched field/claims calibration replaces the synthetic parameters.
TCWS2-C002 | tropical_cyclone_wind | Model v2.0 is a major behavior change because it adds architecture-specific normalized-demand routes and generic fixed/tracker failure-unit outputs. | governance_decision | GOVERNANCE_CONTRACT | CHANGE_CLASSIFICATION model-v2 docs-r1 § Why this is a major model change | T4_placeholder_or_expert_judgment | semantic_damage_model_version=model v2.0 | adopt | Keep v0.1 and v1 artifacts unchanged while researching v2. | Call the change docs-only or silently overwrite v1. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Version policy or runtime behavior changes.
TCWS2-C003 | tropical_cyclone_wind | The Perry 13-knot source route is carried byte-for-value and remains source specific. | governance_decision | TCWS-S020;TCWS-S021 | derivation dossier §12 Perry preservation | T3_engineering_proxy_or_adjacent_empirical | Perry_compatibility_route | adopt | Use the route only with its exact axis, range, and six acknowledgements. | Alias it to generic fixed tilt or ordinary Hazard gust. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | The Perry source package or v1 governed fit changes.
TCWS2-C004 | tropical_cyclone_wind | A failure-state probability becomes DR only through explicit exact-state probabilities and separately listed same-unit state-cost ratios. | governance_decision | GOVERNANCE_CONTRACT;NO_DIRECT_TC_CALIBRATION_SOURCE | derivation dossier §8 Curve form and probability-to-DR typing | T4_placeholder_or_expert_judgment | sum_state_probability_times_cost_ratio | adopt | Audit the probability-to-consequence bridge parameter by parameter. | Relabel Ceferino extensive-failure probability or another exceedance probability as DR. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Observed same-unit state costs replace the T4 ratios.
TCWS2-C005 | tropical_cyclone_wind | All generic beta, medians, and state cost ratios are synthetic T4 assumptions. | governance_decision | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;NO_DIRECT_TC_CALIBRATION_SOURCE | derivation dossier §§7-9 and parameter-tier register TCWS2 curve rows | T4_placeholder_or_expert_judgment | generic_curve_parameters | adopt | Use them as unweighted research scenarios with always-on limitations. | Treat them as fitted estimates, percentiles, posterior draws, or uncertainty bands. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Calibration or structured elicitation is completed.
TCWS2-C006 | tropical_cyclone_wind | After the cell-local T4 values are adopted, the shared profile provides an audit-only cross-hazard comparison fingerprint. | governance_decision | SHARED_SOLAR_WIND_PROXY_V0_1;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;TCWS-S015;GOVERNANCE_CONTRACT | DECISION_LOG model-v2 docs-r1 § TCWS2-D003 | T4_placeholder_or_expert_judgment | audit_comparison_profile_only | adopt | Compare the adopted cell-local parameter payload to the pinned hazard-neutral solar profile. | Load the candidate as a runtime dependency or claim numerical evidence transfer from convective wind. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A formal equivalence or hazard-specific response calibration changes the reuse decision.
TCWS2-C007 | tropical_cyclone_wind | Historical v0.1/v1 claims remain source-version facts and are scoped by the complete v2 supersession map. | governance_decision | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;GOVERNANCE_CONTRACT | CLAIM_SUPERSESSION_MAP model-v2 docs-r1 complete file | T4_placeholder_or_expert_judgment | historical_claim_scope | adopt | Apply each prior claim only to its recorded model/docs scope and retain its evidence limitation. | Treat historical withhold/version statements as the active v2 output contract or erase their retained scientific truth. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A later model version explicitly replaces the map.
TCWS2-C008 | tropical_cyclone_wind | Fixed tilt requires a qualified same-zone TC event/design pressure ratio or a fully bridged array-height speed-squared proxy. | governance_decision | TCWS-S005;TCWS-S010;GOVERNANCE_CONTRACT | derivation dossier §6.1 Fixed tilt | T3_engineering_proxy_or_adjacent_empirical | fixed_axis_contract | adopt | Use a named wind-field, direction, duration, and aerodynamic bridge. | Pass an ordinary 10 m gust directly or call design wind failure capacity. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A validated direct local-demand adapter replaces the proxy.
TCWS2-C009 | tropical_cyclone_wind | Tracker evaluation requires exact-system Ucrit and attained state matched to the qualification basis. | governance_decision | TCWS-S006;TCWS-S007;TCWS-S011;TCWS-S012 | derivation dossier §6.2 Tracker and metadata contract tracker request | T2_public_lab_standard_or_physics | tracker_axis_contract | adopt | Evaluate Vnormal/Ucrit only after exact configuration, layout, angle, position, zone, lock, duration, direction, and speed-reference matching. | Use generic Ucrit, command-only stow, fixed-to-tracker fallback, or a stow multiplier. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Architecture-matched TC tracker calibration becomes available.
TCWS2-C010 | tropical_cyclone_wind | The 0.75 Ucrit rule is an operational-action flag and never a damage threshold. | governance_decision | TCWS-S006 | metadata contract § Tracker route | T2_public_lab_standard_or_physics | stow_action_flag | adopt | Emit a warning flag after qualification matching. | Force damage, force zero damage, or assign mitigation credit at 0.75 Ucrit. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A source calibrates damage conditional on the action threshold.
TCWS2-C011 | tropical_cyclone_wind | Generic ordered-state curves have exact zero only at zero normalized demand and no positive hard-zero threshold. | governance_decision | GOVERNANCE_CONTRACT;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | DECISION_LOG model-v2 docs-r1 § TCWS2-D005 | T4_placeholder_or_expert_judgment | zero_demand_boundary | adopt | Use the native lognormal state form without intercept subtraction. | Claim immunity below an invented threshold or alter the asymptote by anchoring subtraction. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A calibrated physical threshold is adopted.
TCWS2-C012 | tropical_cyclone_wind | Unsupported physical units remain null, not zero. | governance_decision | GOVERNANCE_CONTRACT | DECISION_LOG model-v2 docs-r1 § TCWS2-D006 | T4_placeholder_or_expert_judgment | withhold_not_zero | adopt | Expose incomplete plant coverage and withhold aggregate physical loss. | Assign zero DR to absent curves or recreate the legacy 42-percent immune remainder. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Each unit receives a governed curve or an evidence-backed near-zero treatment.
TCWS2-C013 | tropical_cyclone_wind | PV_GSU_SUBSTATION is a separately located yard/point unit and inherits neither array DR nor exposure. | governance_decision | TCWS-S004;GOVERNANCE_CONTRACT | DECISION_LOG model-v2 docs-r1 § TCWS2-D008 | T3_engineering_proxy_or_adjacent_empirical | GSU_withholding | adopt | Retain identity, value, and acquisition fields for a future GSU route. | Copy flood, wind-farm, legacy substation, array module, or mounting response. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Matched TC-wind GSU demand, disposition, cost, and value evidence arrives.
TCWS2-C014 | tropical_cyclone_wind | Scenario dollars and whole-plant DR remain withheld even for valid generic curves. | governance_decision | GOVERNANCE_CONTRACT;NO_DIRECT_TC_CALIBRATION_SOURCE | derivation dossier §13 Capability and reportability | T4_placeholder_or_expert_judgment | scenario_loss_withheld | historical_scope_only | Use scalar/state DRs only for research and interface testing. | Multiply by TIV or reference values and report economic loss. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. Superseded for model v2.1 runtime behavior by TCWS21-C001/003/004/005; retained only to preserve the prior-version decision trail. | Same-unit state costs, values, exposure, support, and full coverage pass review.
TCWS2-C015 | tropical_cyclone_wind | TC duration, direction evolution, cycling, rain, debris, tornado, flood, and surge have no numerical modifier in v2. | governance_decision | TCWS-S004;TCWS-S025;TCWS-S026;GOVERNANCE_CONTRACT | neighboring-wind and compound-boundary memo § Compound occurrence | T3_engineering_proxy_or_adjacent_empirical | conditioner_and_compound_boundary | adopt | Carry them as bridge inputs, flags, or separate pathways under one event family. | Stack an uncalibrated uplift/discount or double count physical loss. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Pathway-specific calibration and precedence rules pass review.
TCWS2-C016 | tropical_cyclone_wind | The old legacy asset DR is denominator- and coverage-incompatible with v2 failure-unit DR. | governance_decision | LEG-TCWS-001;LEG-TCWS-002;GOVERNANCE_CONTRACT | legacy and adjacent-model audit § Legacy hurricane-solar implementation | T4_placeholder_or_expert_judgment | old_new_comparison_rule | adopt | Preserve the old curve only as a migration fixture and compare behavior qualitatively. | Claim a v2 increase/decrease without matching axis, unit, denominator, and covered value. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | A common scenario assembly with complete coverage is governed.
TCWS2-C017 | tropical_cyclone_wind | The v2 artifact remains absent from current/, the artifact index, package releases, and Hazard cutover. | governance_decision | GOVERNANCE_CONTRACT | DECISION_LOG model-v2 docs-r1 § TCWS2-D009 | T4_placeholder_or_expert_judgment | promotion_status | adopt | Review and validate the proposal without changing consumer state. | Load it as canonical merely because it exists in the repository. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | Every promotion gate and maintainer decision closes.
TCWS2-C018 | tropical_cyclone_wind | The v2 supersession map is mandatory provenance for every consolidated historical claim whose output or version conclusion differs in v2. | governance_decision | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION;GOVERNANCE_CONTRACT | CLAIM_SUPERSESSION_MAP model-v2 docs-r1 complete file | T4_placeholder_or_expert_judgment | claim_supersession_map_required | adopt | Use the map to distinguish retained evidence limitations from superseded noncanonical output behavior. | Read the consolidated register as if every row were simultaneously active for model v2. | The v2 package prioritizes explicit coverage while keeping missing calibration visible and machine enforced. | The consolidated-register format gains native version-scope and supersession fields.
TCWS21-C001 | tropical_cyclone_wind | A screening v2 must return a complete physical-damage view rather than convert unsupported value to zero or leave the requested plant output unavailable. | governed_model_decision | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | DECISION_LOG_tropical_cyclone_wind_solar__model_v2_1__docs_r1.md#decision-1 | T4 | coverage_complete_screening_contract | adopted_model_v2_1 | v2.1 may use explicit labeled proxy curves to complete screening coverage | proxy status does not imply calibration or canonical promotion | The requested product is a usable screening curve; v2.0 governance prevented that use. | replace proxies when matched unit-level TC evidence or elicitation is available
TCWS21-C002 | tropical_cyclone_wind | The named NLR physical-value profile reconciles 100% of the 877.7957023626668 USD/kWdc physical replacement basis when direct/civil units and support-once value are assembled. | reproducible_value_reconciliation | TCWS2-S013 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map rows 2-17 | T2 | reference_value_profile | adopted_model_v2_1 | named reference-profile physical DR and loss per kWdc | site-specific TIV accuracy without replacement by site values | A named profile makes the screening assembly explicit, reproducible, and usable. | governed site-specific value profile or updated benchmark
TCWS21-C003 | tropical_cyclone_wind | Foundation, power/collection, GSU, SCADA, and civil infrastructure each return an explicit Tier-4 same-unit screening DR on the qualified site-facility wind-demand axis. | governed_model_decision | TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | DECISION_LOG_tropical_cyclone_wind_solar__model_v2_1__docs_r1.md#decision-2 | T4 | common_failure_unit_numeric_coverage | adopted_model_v2_1 | numeric wind-only screening DR for each named same-unit failure unit | calibrated claims response, flood response, or transfer to another asset anatomy | Explicit proxies make the requested screening product usable while preserving unit identity and evidence grade. | matched unit-level TC evidence or formal elicitation replaces a proxy record
TCWS21-C004 | tropical_cyclone_wind | Replacement support is allocated exactly once using the value-weighted direct-and-civil DR; it is not an intrinsic independently damaged unit. | governed_assembly_rule | GOVERNANCE_CONTRACT;TCWS2-S013 | DECISION_LOG_tropical_cyclone_wind_solar__model_v2_1__docs_r1.md#decision-3 | T4 | replacement_support_allocate_once | adopted_model_v2_1 | complete named-profile physical loss without double-counting replacement support | an independent support fragility curve or repeated support loading across failure units | The assembly needs full value coverage and must avoid multiplying the same support value by several unit DRs. | a governed support-cost allocation model supersedes the screening rule
TCWS21-C005 | tropical_cyclone_wind | Model v2.1 supports failure-unit DR, full-plant physical replacement DR, physical loss per kWdc, installed-capex physical loss fraction, and scenario physical dollars when capacity is supplied. | runtime_output_contract | GOVERNANCE_CONTRACT;TCWS2_CELL_LOCAL_SYNTHETIC_DECISION | tropical_cyclone_wind_solar__model_v2_1__docs_r1__curve_artifact.json::emit_contract | T4 | v2_1_supported_outputs | adopted_model_v2_1 | the listed event physical-damage outputs for a valid exact-pinned screening call | EAL, PML, VaR, TVaR, BI, downtime, or excluded compound-pathway loss from the Damage artifact alone | Usability requires numeric event damage and value outputs; annual and disruption metrics remain separate typed stages. | a governed output-contract revision changes the supported result set

## Old_vs_New
architecture | array_demand_ratio | site_demand_ratio | model_v2_0_full_plant_dr | model_v2_1_lower_resistance_physical_dr | model_v2_1_central_physical_dr | model_v2_1_upper_resistance_physical_dr | reason
fixed_tilt | 0 | 0 | WITHHELD | 0 | 0 | 0 | coverage-complete common-unit proxies plus named value assembly
fixed_tilt | 0.5 | 0.5 | WITHHELD | 0.017978 | 0.0039107 | 0.00072101 | coverage-complete common-unit proxies plus named value assembly
fixed_tilt | 1 | 1 | WITHHELD | 0.33357 | 0.14417 | 0.056245 | coverage-complete common-unit proxies plus named value assembly
fixed_tilt | 1.5 | 1.5 | WITHHELD | 0.76503 | 0.5083 | 0.27311 | coverage-complete common-unit proxies plus named value assembly
fixed_tilt | 2 | 2 | WITHHELD | 0.93987 | 0.80344 | 0.57679 | coverage-complete common-unit proxies plus named value assembly
tracker | 0 | 0 | WITHHELD | 0 | 0 | 0 | coverage-complete common-unit proxies plus named value assembly
tracker | 0.5 | 0.5 | WITHHELD | 0.011109 | 0.002666 | 0.00052502 | coverage-complete common-unit proxies plus named value assembly
tracker | 1 | 1 | WITHHELD | 0.34397 | 0.15813 | 0.061102 | coverage-complete common-unit proxies plus named value assembly
tracker | 1.5 | 1.5 | WITHHELD | 0.79636 | 0.58165 | 0.34411 | coverage-complete common-unit proxies plus named value assembly
tracker | 2 | 2 | WITHHELD | 0.95134 | 0.85554 | 0.67611 | coverage-complete common-unit proxies plus named value assembly

## Plant_Curve_Table
architecture | array_demand_ratio | site_facility_demand_ratio | scenario_id | physical_replacement_dr | physical_loss_2024_usd_per_kwdc | installed_capex_physical_loss_fraction
fixed_tilt | 0 | 0 | central_screening | 0 | 0 | 0
fixed_tilt | 0 | 0 | lower_resistance | 0 | 0 | 0
fixed_tilt | 0 | 0 | upper_resistance | 0 | 0 | 0
fixed_tilt | 0.05 | 0.05 | central_screening | 7.2141e-18 | 6.3325e-15 | 5.654e-18
fixed_tilt | 0.05 | 0.05 | lower_resistance | 1.0292e-15 | 9.0345e-13 | 8.0665e-16
fixed_tilt | 0.05 | 0.05 | upper_resistance | 3.4345e-20 | 3.0148e-17 | 2.6918e-20
fixed_tilt | 0.1 | 0.1 | central_screening | 1.0135e-11 | 8.8969e-09 | 7.9436e-12
fixed_tilt | 0.1 | 0.1 | lower_resistance | 4.5047e-10 | 3.9542e-07 | 3.5305e-10
fixed_tilt | 0.1 | 0.1 | upper_resistance | 1.5898e-13 | 1.3955e-10 | 1.246e-13
fixed_tilt | 0.15 | 0.15 | central_screening | 7.4602e-09 | 6.5485e-06 | 5.8469e-09
fixed_tilt | 0.15 | 0.15 | lower_resistance | 1.8361e-07 | 0.00016117 | 1.439e-07
fixed_tilt | 0.15 | 0.15 | upper_resistance | 2.2929e-10 | 2.0127e-07 | 1.7971e-10
fixed_tilt | 0.2 | 0.2 | central_screening | 4.0088e-07 | 0.00035189 | 3.1418e-07
fixed_tilt | 0.2 | 0.2 | lower_resistance | 6.9732e-06 | 0.006121 | 5.4652e-06
fixed_tilt | 0.2 | 0.2 | upper_resistance | 1.9277e-08 | 1.6921e-05 | 1.5108e-08
fixed_tilt | 0.25 | 0.25 | central_screening | 6.1209e-06 | 0.0053729 | 4.7972e-06
fixed_tilt | 0.25 | 0.25 | lower_resistance | 8.1556e-05 | 0.07159 | 6.3919e-05
fixed_tilt | 0.25 | 0.25 | upper_resistance | 4.0738e-07 | 0.0003576 | 3.1928e-07
fixed_tilt | 0.3 | 0.3 | central_screening | 4.5262e-05 | 0.039731 | 3.5474e-05
fixed_tilt | 0.3 | 0.3 | lower_resistance | 0.0004705 | 0.41301 | 0.00036875
fixed_tilt | 0.3 | 0.3 | upper_resistance | 3.9033e-06 | 0.0034263 | 3.0592e-06
fixed_tilt | 0.35 | 0.35 | central_screening | 0.0002088 | 0.18328 | 0.00016364
fixed_tilt | 0.35 | 0.35 | lower_resistance | 0.0017119 | 1.5027 | 0.0013417
fixed_tilt | 0.35 | 0.35 | upper_resistance | 2.2501e-05 | 0.019751 | 1.7635e-05
fixed_tilt | 0.4 | 0.4 | central_screening | 0.0006919 | 0.60735 | 0.00054228
fixed_tilt | 0.4 | 0.4 | lower_resistance | 0.0045561 | 3.9993 | 0.0035708
fixed_tilt | 0.4 | 0.4 | upper_resistance | 9.0963e-05 | 0.079847 | 7.1292e-05
fixed_tilt | 0.45 | 0.45 | central_screening | 0.0018005 | 1.5805 | 0.0014111
fixed_tilt | 0.45 | 0.45 | lower_resistance | 0.0097645 | 8.5712 | 0.0076529
fixed_tilt | 0.45 | 0.45 | upper_resistance | 0.00028302 | 0.24844 | 0.00022182
fixed_tilt | 0.5 | 0.5 | central_screening | 0.0039107 | 3.4328 | 0.003065
fixed_tilt | 0.5 | 0.5 | lower_resistance | 0.017978 | 15.7806 | 0.01409
fixed_tilt | 0.5 | 0.5 | upper_resistance | 0.00072101 | 0.6329 | 0.00056509
fixed_tilt | 0.55 | 0.55 | central_screening | 0.0074072 | 6.502 | 0.0058053
fixed_tilt | 0.55 | 0.55 | lower_resistance | 0.029718 | 26.0865 | 0.023292
fixed_tilt | 0.55 | 0.55 | upper_resistance | 0.0015715 | 1.3795 | 0.0012317
fixed_tilt | 0.6 | 0.6 | central_screening | 0.012636 | 11.0915 | 0.0099031
fixed_tilt | 0.6 | 0.6 | lower_resistance | 0.045452 | 39.8977 | 0.035623
fixed_tilt | 0.6 | 0.6 | upper_resistance | 0.0030282 | 2.6581 | 0.0023733
fixed_tilt | 0.65 | 0.65 | central_screening | 0.019887 | 17.457 | 0.015587
fixed_tilt | 0.65 | 0.65 | lower_resistance | 0.065611 | 57.5935 | 0.051423
fixed_tilt | 0.65 | 0.65 | upper_resistance | 0.0052886 | 4.6423 | 0.0041449
fixed_tilt | 0.7 | 0.7 | central_screening | 0.029408 | 25.8145 | 0.023049
fixed_tilt | 0.7 | 0.7 | lower_resistance | 0.09055 | 79.4845 | 0.070968
fixed_tilt | 0.7 | 0.7 | upper_resistance | 0.0085358 | 7.4927 | 0.0066899
fixed_tilt | 0.75 | 0.75 | central_screening | 0.041415 | 36.3536 | 0.032459
fixed_tilt | 0.75 | 0.75 | lower_resistance | 0.12046 | 105.7394 | 0.09441
fixed_tilt | 0.75 | 0.75 | upper_resistance | 0.012929 | 11.3487 | 0.010133
fixed_tilt | 0.8 | 0.8 | central_screening | 0.056101 | 49.2451 | 0.043969
fixed_tilt | 0.8 | 0.8 | lower_resistance | 0.15529 | 136.3153 | 0.12171
fixed_tilt | 0.8 | 0.8 | upper_resistance | 0.018601 | 16.3281 | 0.014579
fixed_tilt | 0.85 | 0.85 | central_screening | 0.073634 | 64.6353 | 0.05771
fixed_tilt | 0.85 | 0.85 | lower_resistance | 0.19472 | 170.9235 | 0.15261
fixed_tilt | 0.85 | 0.85 | upper_resistance | 0.025669 | 22.5319 | 0.020118
fixed_tilt | 0.9 | 0.9 | central_screening | 0.094134 | 82.6307 | 0.073777
fixed_tilt | 0.9 | 0.9 | lower_resistance | 0.23814 | 209.0386 | 0.18664
fixed_tilt | 0.9 | 0.9 | upper_resistance | 0.034235 | 30.0513 | 0.026831
fixed_tilt | 0.95 | 0.95 | central_screening | 0.11766 | 103.2789 | 0.092213
fixed_tilt | 0.95 | 0.95 | lower_resistance | 0.28474 | 249.9445 | 0.22316
fixed_tilt | 0.95 | 0.95 | upper_resistance | 0.044397 | 38.9712 | 0.034796
fixed_tilt | 1 | 1 | central_screening | 0.14417 | 126.5514 | 0.11299
fixed_tilt | 1 | 1 | lower_resistance | 0.33357 | 292.8029 | 0.26143
fixed_tilt | 1 | 1 | upper_resistance | 0.056245 | 49.372 | 0.044082
fixed_tilt | 1.05 | 1.05 | central_screening | 0.17354 | 152.3341 | 0.13601
fixed_tilt | 1.05 | 1.05 | lower_resistance | 0.38361 | 336.7275 | 0.30065
fixed_tilt | 1.05 | 1.05 | upper_resistance | 0.069864 | 61.3263 | 0.054756
fixed_tilt | 1.1 | 1.1 | central_screening | 0.20554 | 180.4259 | 0.16109
fixed_tilt | 1.1 | 1.1 | lower_resistance | 0.43387 | 380.8522 | 0.34005
fixed_tilt | 1.1 | 1.1 | upper_resistance | 0.085319 | 74.8931 | 0.066869
fixed_tilt | 1.15 | 1.15 | central_screening | 0.23986 | 210.5471 | 0.18799
fixed_tilt | 1.15 | 1.15 | lower_resistance | 0.48347 | 424.3847 | 0.37891
fixed_tilt | 1.15 | 1.15 | upper_resistance | 0.10266 | 90.1116 | 0.080457
fixed_tilt | 1.2 | 1.2 | central_screening | 0.27609 | 242.3539 | 0.21639
fixed_tilt | 1.2 | 1.2 | lower_resistance | 0.53161 | 466.6433 | 0.41665
fixed_tilt | 1.2 | 1.2 | upper_resistance | 0.12189 | 106.9941 | 0.09553
fixed_tilt | 1.25 | 1.25 | central_screening | 0.31381 | 275.4576 | 0.24594
fixed_tilt | 1.25 | 1.25 | lower_resistance | 0.57767 | 507.0762 | 0.45275
fixed_tilt | 1.25 | 1.25 | upper_resistance | 0.143 | 125.5213 | 0.11207
fixed_tilt | 1.3 | 1.3 | central_screening | 0.35253 | 309.4452 | 0.27629
fixed_tilt | 1.3 | 1.3 | lower_resistance | 0.62118 | 545.2673 | 0.48685
fixed_tilt | 1.3 | 1.3 | upper_resistance | 0.16591 | 145.6386 | 0.13003
fixed_tilt | 1.35 | 1.35 | central_screening | 0.39178 | 343.8998 | 0.30705
fixed_tilt | 1.35 | 1.35 | lower_resistance | 0.66181 | 580.9302 | 0.51869
fixed_tilt | 1.35 | 1.35 | upper_resistance | 0.19054 | 167.2564 | 0.14934
fixed_tilt | 1.4 | 1.4 | central_screening | 0.4311 | 378.4179 | 0.33787
fixed_tilt | 1.4 | 1.4 | lower_resistance | 0.69936 | 613.8958 | 0.54812
fixed_tilt | 1.4 | 1.4 | upper_resistance | 0.21674 | 190.2515 | 0.16987
fixed_tilt | 1.45 | 1.45 | central_screening | 0.47007 | 412.6243 | 0.36841
fixed_tilt | 1.45 | 1.45 | lower_resistance | 0.73376 | 644.0954 | 0.57509
fixed_tilt | 1.45 | 1.45 | upper_resistance | 0.24433 | 214.4709 | 0.19149
fixed_tilt | 1.5 | 1.5 | central_screening | 0.5083 | 446.1823 | 0.39838
fixed_tilt | 1.5 | 1.5 | lower_resistance | 0.76503 | 671.5418 | 0.59959
fixed_tilt | 1.5 | 1.5 | upper_resistance | 0.27311 | 239.7379 | 0.21405
fixed_tilt | 1.55 | 1.55 | central_screening | 0.54546 | 478.8011 | 0.4275
fixed_tilt | 1.55 | 1.55 | lower_resistance | 0.79325 | 696.3116 | 0.62171
fixed_tilt | 1.55 | 1.55 | upper_resistance | 0.30287 | 265.8576 | 0.23737
fixed_tilt | 1.6 | 1.6 | central_screening | 0.58127 | 510.2388 | 0.45557
fixed_tilt | 1.6 | 1.6 | lower_resistance | 0.81856 | 718.5281 | 0.64154
fixed_tilt | 1.6 | 1.6 | upper_resistance | 0.33336 | 292.624 | 0.26127
fixed_tilt | 1.65 | 1.65 | central_screening | 0.61552 | 540.3036 | 0.48241
fixed_tilt | 1.65 | 1.65 | lower_resistance | 0.84114 | 738.3463 | 0.65924
fixed_tilt | 1.65 | 1.65 | upper_resistance | 0.36435 | 319.827 | 0.28556
fixed_tilt | 1.7 | 1.7 | central_screening | 0.64805 | 568.8514 | 0.5079
fixed_tilt | 1.7 | 1.7 | lower_resistance | 0.86118 | 755.9411 | 0.67495
fixed_tilt | 1.7 | 1.7 | upper_resistance | 0.3956 | 347.2577 | 0.31005
fixed_tilt | 1.75 | 1.75 | central_screening | 0.67873 | 595.7831 | 0.53195
fixed_tilt | 1.75 | 1.75 | lower_resistance | 0.8789 | 771.497 | 0.68884
fixed_tilt | 1.75 | 1.75 | upper_resistance | 0.42688 | 374.7144 | 0.33457
fixed_tilt | 1.8 | 1.8 | central_screening | 0.7075 | 621.0396 | 0.5545
fixed_tilt | 1.8 | 1.8 | lower_resistance | 0.89451 | 785.2004 | 0.70107
fixed_tilt | 1.8 | 1.8 | upper_resistance | 0.45797 | 402.0069 | 0.35893
fixed_tilt | 1.85 | 1.85 | central_screening | 0.73434 | 644.5971 | 0.57553
fixed_tilt | 1.85 | 1.85 | lower_resistance | 0.90822 | 797.234 | 0.71182
fixed_tilt | 1.85 | 1.85 | upper_resistance | 0.48868 | 428.9602 | 0.383
fixed_tilt | 1.9 | 1.9 | central_screening | 0.75924 | 666.4618 | 0.59506
fixed_tilt | 1.9 | 1.9 | lower_resistance | 0.92023 | 807.7727 | 0.72123
fixed_tilt | 1.9 | 1.9 | upper_resistance | 0.51882 | 455.4165 | 0.40662
fixed_tilt | 1.95 | 1.95 | central_screening | 0.78226 | 686.664 | 0.61309
fixed_tilt | 1.95 | 1.95 | lower_resistance | 0.93072 | 816.9806 | 0.72945
fixed_tilt | 1.95 | 1.95 | upper_resistance | 0.54823 | 481.2374 | 0.42968
fixed_tilt | 2 | 2 | central_screening | 0.80344 | 705.254 | 0.62969
fixed_tilt | 2 | 2 | lower_resistance | 0.93987 | 825.0098 | 0.73662
fixed_tilt | 2 | 2 | upper_resistance | 0.57679 | 506.3042 | 0.45206
tracker | 0 | 0 | central_screening | 0 | 0 | 0
tracker | 0 | 0 | lower_resistance | 0 | 0 | 0
tracker | 0 | 0 | upper_resistance | 0 | 0 | 0
tracker | 0.05 | 0.05 | central_screening | 7.214e-18 | 6.3324e-15 | 5.6539e-18
tracker | 0.05 | 0.05 | lower_resistance | 1.029e-15 | 9.0322e-13 | 8.0645e-16
tracker | 0.05 | 0.05 | upper_resistance | 3.4345e-20 | 3.0148e-17 | 2.6918e-20
tracker | 0.1 | 0.1 | central_screening | 1.0115e-11 | 8.8787e-09 | 7.9274e-12
tracker | 0.1 | 0.1 | lower_resistance | 4.4117e-10 | 3.8725e-07 | 3.4576e-10
tracker | 0.1 | 0.1 | upper_resistance | 1.5888e-13 | 1.3946e-10 | 1.2452e-13
tracker | 0.15 | 0.15 | central_screening | 7.3043e-09 | 6.4116e-06 | 5.7247e-09
tracker | 0.15 | 0.15 | lower_resistance | 1.6203e-07 | 0.00014223 | 1.2699e-07
tracker | 0.15 | 0.15 | upper_resistance | 2.2744e-10 | 1.9964e-07 | 1.7825e-10
tracker | 0.2 | 0.2 | central_screening | 3.7121e-07 | 0.00032585 | 2.9093e-07
tracker | 0.2 | 0.2 | lower_resistance | 5.1703e-06 | 0.0045385 | 4.0522e-06
tracker | 0.2 | 0.2 | upper_resistance | 1.8601e-08 | 1.6328e-05 | 1.4578e-08
tracker | 0.25 | 0.25 | central_screening | 5.1863e-06 | 0.0045525 | 4.0647e-06
tracker | 0.25 | 0.25 | lower_resistance | 5.1172e-05 | 0.044919 | 4.0106e-05
tracker | 0.25 | 0.25 | upper_resistance | 3.7242e-07 | 0.00032691 | 2.9188e-07
tracker | 0.3 | 0.3 | central_screening | 3.4815e-05 | 0.030561 | 2.7286e-05
tracker | 0.3 | 0.3 | lower_resistance | 0.00026409 | 0.23181 | 0.00020698
tracker | 0.3 | 0.3 | upper_resistance | 3.3228e-06 | 0.0029167 | 2.6042e-06
tracker | 0.35 | 0.35 | central_screening | 0.00014843 | 0.13029 | 0.00011633
tracker | 0.35 | 0.35 | lower_resistance | 0.00091853 | 0.80628 | 0.00071989
tracker | 0.35 | 0.35 | upper_resistance | 1.7853e-05 | 0.015671 | 1.3992e-05
tracker | 0.4 | 0.4 | central_screening | 0.00046943 | 0.41206 | 0.00036791
tracker | 0.4 | 0.4 | lower_resistance | 0.0024747 | 2.1723 | 0.0019395
tracker | 0.4 | 0.4 | upper_resistance | 6.8421e-05 | 0.06006 | 5.3625e-05
tracker | 0.45 | 0.45 | central_screening | 0.0012067 | 1.0592 | 0.00094573
tracker | 0.45 | 0.45 | lower_resistance | 0.0055913 | 4.908 | 0.0043821
tracker | 0.45 | 0.45 | upper_resistance | 0.00020688 | 0.1816 | 0.00016214
tracker | 0.5 | 0.5 | central_screening | 0.002666 | 2.3402 | 0.0020894
tracker | 0.5 | 0.5 | lower_resistance | 0.011109 | 9.7511 | 0.0087063
tracker | 0.5 | 0.5 | upper_resistance | 0.00052502 | 0.46086 | 0.00041148
tracker | 0.55 | 0.55 | central_screening | 0.0052471 | 4.6059 | 0.0041124
tracker | 0.55 | 0.55 | lower_resistance | 0.019998 | 17.5541 | 0.015673
tracker | 0.55 | 0.55 | upper_resistance | 0.0011634 | 1.0212 | 0.00091178
tracker | 0.6 | 0.6 | central_screening | 0.0094275 | 8.2755 | 0.0073888
tracker | 0.6 | 0.6 | lower_resistance | 0.033276 | 29.2099 | 0.02608
tracker | 0.6 | 0.6 | upper_resistance | 0.0023122 | 2.0297 | 0.0018122
tracker | 0.65 | 0.65 | central_screening | 0.015737 | 13.814 | 0.012334
tracker | 0.65 | 0.65 | lower_resistance | 0.051888 | 45.547 | 0.040667
tracker | 0.65 | 0.65 | upper_resistance | 0.0042043 | 3.6905 | 0.0032951
tracker | 0.7 | 0.7 | central_screening | 0.024727 | 21.7054 | 0.01938
tracker | 0.7 | 0.7 | lower_resistance | 0.076564 | 67.2076 | 0.060007
tracker | 0.7 | 0.7 | upper_resistance | 0.007102 | 6.2341 | 0.0055661
tracker | 0.75 | 0.75 | central_screening | 0.036933 | 32.4196 | 0.028946
tracker | 0.75 | 0.75 | lower_resistance | 0.10769 | 94.5313 | 0.084403
tracker | 0.75 | 0.75 | upper_resistance | 0.011284 | 9.9054 | 0.0088441
tracker | 0.8 | 0.8 | central_screening | 0.052829 | 46.3733 | 0.041405
tracker | 0.8 | 0.8 | lower_resistance | 0.14522 | 127.477 | 0.11382
tracker | 0.8 | 0.8 | upper_resistance | 0.017036 | 14.9545 | 0.013352
tracker | 0.85 | 0.85 | central_screening | 0.072782 | 63.8877 | 0.057043
tracker | 0.85 | 0.85 | lower_resistance | 0.18866 | 165.6047 | 0.14786
tracker | 0.85 | 0.85 | upper_resistance | 0.024639 | 21.6283 | 0.019311
tracker | 0.9 | 0.9 | central_screening | 0.097002 | 85.148 | 0.076025
tracker | 0.9 | 0.9 | lower_resistance | 0.23709 | 208.1192 | 0.18582
tracker | 0.9 | 0.9 | upper_resistance | 0.034362 | 30.1625 | 0.026931
tracker | 0.95 | 0.95 | central_screening | 0.12551 | 110.1744 | 0.09837
tracker | 0.95 | 0.95 | lower_resistance | 0.28932 | 253.9631 | 0.22675
tracker | 0.95 | 0.95 | upper_resistance | 0.046448 | 40.7714 | 0.036403
tracker | 1 | 1 | central_screening | 0.15813 | 138.8096 | 0.12394
tracker | 1 | 1 | lower_resistance | 0.34397 | 301.9344 | 0.26958
tracker | 1 | 1 | upper_resistance | 0.061102 | 53.6352 | 0.047889
tracker | 1.05 | 1.05 | central_screening | 0.19449 | 170.7258 | 0.15243
tracker | 1.05 | 1.05 | lower_resistance | 0.39964 | 350.8057 | 0.31322
tracker | 1.05 | 1.05 | upper_resistance | 0.078476 | 68.8861 | 0.061505
tracker | 1.1 | 1.1 | central_screening | 0.23405 | 205.4495 | 0.18344
tracker | 1.1 | 1.1 | lower_resistance | 0.45503 | 399.4244 | 0.35663
tracker | 1.1 | 1.1 | upper_resistance | 0.098651 | 86.5952 | 0.077317
tracker | 1.15 | 1.15 | central_screening | 0.27614 | 242.3983 | 0.21643
tracker | 1.15 | 1.15 | lower_resistance | 0.50899 | 446.7863 | 0.39892
tracker | 1.15 | 1.15 | upper_resistance | 0.12163 | 106.7624 | 0.095324
tracker | 1.2 | 1.2 | central_screening | 0.32003 | 280.9245 | 0.25083
tracker | 1.2 | 1.2 | lower_resistance | 0.56058 | 492.078 | 0.43936
tracker | 1.2 | 1.2 | upper_resistance | 0.14731 | 129.3118 | 0.11546
tracker | 1.25 | 1.25 | central_screening | 0.36496 | 320.3597 | 0.28604
tracker | 1.25 | 1.25 | lower_resistance | 0.60913 | 534.6928 | 0.4774
tracker | 1.25 | 1.25 | upper_resistance | 0.17554 | 154.0922 | 0.13758
tracker | 1.3 | 1.3 | central_screening | 0.41018 | 360.0533 | 0.32148
tracker | 1.3 | 1.3 | lower_resistance | 0.65417 | 574.2238 | 0.5127
tracker | 1.3 | 1.3 | upper_resistance | 0.20607 | 180.8836 | 0.1615
tracker | 1.35 | 1.35 | central_screening | 0.45501 | 399.405 | 0.35661
tracker | 1.35 | 1.35 | lower_resistance | 0.69543 | 610.444 | 0.54504
tracker | 1.35 | 1.35 | upper_resistance | 0.23856 | 209.4085 | 0.18697
tracker | 1.4 | 1.4 | central_screening | 0.49885 | 437.8871 | 0.39097
tracker | 1.4 | 1.4 | lower_resistance | 0.73283 | 643.2771 | 0.57435
tracker | 1.4 | 1.4 | upper_resistance | 0.27267 | 239.3464 | 0.2137
tracker | 1.45 | 1.45 | central_screening | 0.54119 | 475.0582 | 0.42416
tracker | 1.45 | 1.45 | lower_resistance | 0.76643 | 672.7666 | 0.60068
tracker | 1.45 | 1.45 | upper_resistance | 0.30799 | 270.3495 | 0.24138
tracker | 1.5 | 1.5 | central_screening | 0.58165 | 510.5688 | 0.45586
tracker | 1.5 | 1.5 | lower_resistance | 0.79636 | 699.0443 | 0.62415
tracker | 1.5 | 1.5 | upper_resistance | 0.34411 | 302.0588 | 0.2697
tracker | 1.55 | 1.55 | central_screening | 0.61992 | 544.1596 | 0.48586
tracker | 1.55 | 1.55 | lower_resistance | 0.82286 | 722.3031 | 0.64491
tracker | 1.55 | 1.55 | upper_resistance | 0.38063 | 334.1191 | 0.29832
tracker | 1.6 | 1.6 | central_screening | 0.6558 | 575.6559 | 0.51398
tracker | 1.6 | 1.6 | lower_resistance | 0.84618 | 742.7737 | 0.66319
tracker | 1.6 | 1.6 | upper_resistance | 0.41717 | 366.1915 | 0.32696
tracker | 1.65 | 1.65 | central_screening | 0.68918 | 604.9582 | 0.54014
tracker | 1.65 | 1.65 | lower_resistance | 0.86661 | 760.7053 | 0.6792
tracker | 1.65 | 1.65 | upper_resistance | 0.45337 | 397.9636 | 0.35532
tracker | 1.7 | 1.7 | central_screening | 0.72002 | 632.0315 | 0.56431
tracker | 1.7 | 1.7 | lower_resistance | 0.88443 | 776.3519 | 0.69317
tracker | 1.7 | 1.7 | upper_resistance | 0.4889 | 429.1566 | 0.38318
tracker | 1.75 | 1.75 | central_screening | 0.74834 | 656.893 | 0.58651
tracker | 1.75 | 1.75 | lower_resistance | 0.89994 | 789.9621 | 0.70532
tracker | 1.75 | 1.75 | upper_resistance | 0.5235 | 459.5302 | 0.41029
tracker | 1.8 | 1.8 | central_screening | 0.77421 | 679.6016 | 0.60679
tracker | 1.8 | 1.8 | lower_resistance | 0.91339 | 801.7713 | 0.71587
tracker | 1.8 | 1.8 | upper_resistance | 0.55695 | 488.8845 | 0.4365
tracker | 1.85 | 1.85 | central_screening | 0.79773 | 700.2472 | 0.62522
tracker | 1.85 | 1.85 | lower_resistance | 0.92504 | 811.9985 | 0.725
tracker | 1.85 | 1.85 | upper_resistance | 0.58904 | 517.06 | 0.46166
tracker | 1.9 | 1.9 | central_screening | 0.81903 | 718.9414 | 0.64191
tracker | 1.9 | 1.9 | lower_resistance | 0.93512 | 820.843 | 0.7329
tracker | 1.9 | 1.9 | upper_resistance | 0.61966 | 543.9361 | 0.48566
tracker | 1.95 | 1.95 | central_screening | 0.83825 | 735.8097 | 0.65697
tracker | 1.95 | 1.95 | lower_resistance | 0.94382 | 828.4844 | 0.73972
tracker | 1.95 | 1.95 | upper_resistance | 0.6487 | 569.4284 | 0.50842
tracker | 2 | 2 | central_screening | 0.85554 | 750.9855 | 0.67052
tracker | 2 | 2 | lower_resistance | 0.95134 | 835.0824 | 0.74561
tracker | 2 | 2 | upper_resistance | 0.67611 | 593.4851 | 0.5299

## KATs
test_id | type | status_or_error
TCWS21-FIXED-ZERO | runtime | PASS_EXPECTED
TCWS21-FIXED-CENTRAL | runtime | PASS_EXPECTED
TCWS21-FIXED-HIGH | runtime | PASS_EXPECTED
TCWS21-TRACKER-CENTRAL | runtime | PASS_EXPECTED
TCWS21-GSU-DIRECT | runtime | PASS_EXPECTED
TCWS21-REJECT-MISSING-SITE-AXIS | rejection | SITE_AXIS_PAYLOAD_REQUIRED
TCWS21-REJECT-VALUE-PROFILE | rejection | VALUE_PROFILE_UNSUPPORTED
TCWS21-REJECT-NO-MODE-OR-UNIT | rejection | OUTPUT_MODE_REQUIRED
TCWS21-REJECT-DIRECT-SUPPORT | rejection | DERIVED_ASSEMBLY_RULE_ONLY
TCWS21-REJECT-SITE-RANGE | rejection | SITE_AXIS_OUTSIDE_VALID_RANGE

## QA
check | observed | expected | status
model | model v2.1 | model v2.1 | PASS
curve records | 10 | 10 | PASS
common curves | 5 | 5 | PASS
withheld units | 0 | 0 | PASS
scenario loss support | supported_with_explicit_failure_unit_value_and_exposure_basis | supported_with_explicit_failure_unit_value_and_exposure_basis | PASS
physical value | 877.7957 | 877.7957 | PASS
runtime KATs | 5 | 5 | PASS
rejection KATs | 5 | 5 | PASS