## README
Tropical-cyclone wind × onshore wind — governed v1 workbook
Model v1.0/docs r1 • noncanonical release candidate • three exact Jaimes source archetypes • partial failure-unit coverage
Identity | Value | Order | Sheet | Purpose
Cell ID | tropical_cyclone_wind_wind | 1 | README | Identity, status, and map
Damage code ID | TROPICAL_CYCLONE_WIND_WIND_JAIMES_SCREENING_V1 | 2 | Scope_Coverage | Included pathway and explicit exclusions
Semantic model | model v1.0 | 3 | Inputs | Source-native selectors and curve parameters
Documentation | docs r1 | 4 | Jaimes_Curves | Formula-driven curve audit and chart
Lifecycle | release_candidate / proposed | 5 | Failure_Units | Supported atom and all withheld plant units
Runtime curve count | 3 | 6 | Value_Crosswalk | Source denominator quarantine and non-mappings
Canonical runtime artifact | FALSE | 7 | Old_vs_New | Migration comparison without false equivalence
Model grade | screening_source_derived_engineering_proxy | 8 | KATs | Formula-known-answer reproduction
Supported atom | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | 9 | Source_Register | Evidence, locators, and permitted inference
Whole-farm/scenario loss | WITHHELD | 10 | Claim_Register | Governed claims and prohibitions
Consumer action | Do not cut over until every promotion gate passes | 11 | Parameter_Tiers | Parameter tiers and update triggers
|  | 12 | QA | Formula-driven workbook assertions
Release boundary: scalar DR is conditional on an exact Jaimes archetype, exact source-model assumption set, and native 3-second gust at 10 m. Dollar loss, whole-turbine loss, whole-plant loss, EAL/PML/VaR/TVaR, and every uncovered failure unit remain null/withheld—not zero.

## Scope_Coverage
Scope and coverage boundary
Direct TC aerodynamic loading only; pathway identity and value grain are part of the contract.
Dimension | Included/supported | Excluded/withheld | Runtime behavior | Why | Promotion dependency | Source/contract
Hazard pathway | tropical_cyclone_wind direct aerodynamic loading | TC-spawned tornado; windborne debris impact; wind-driven rain ingress; storm surge; pluvial flood; scour or saturated-soil failure; lightning or fire; offshore wave and support loading; business interruption or curtailment | Exact pathway only | Avoid compound-event and tornado substitution | Hazard pathway router | Bundle v3 draft
Axis | 3-second peak gust at 10 m, km/h | NHC 1-minute sustained, category, hub wind, terrain/height/time proxies | Reject without named bridge | Axes are not interchangeable | Validated Hazard axis adapter | Jaimes 2020; NHC glossary
Range | V<=90 source-assumed zero; 108–252 evaluated | 90<V<108 and V>252 | Withhold outside governed branches | Simulation range starts at 108 km/h | Independent reproduction | Jaimes 2020
Asset selector | Three exact generic source archetypes | Nearest, interpolation, modern-fleet transfer | Exact selector match | No transfer evidence | Engineering applicability review | Artifact selector contract
Failure unit | Jaimes turbine/tower exposure record | Standard turbine assembly and all BOS/civil/support units | Conditional scalar DR only | Source denominator and component coverage are unresolved | Value and engineering review | Cell package
Value | Paper-native Ct(h) audit proxy | CWER tower/equipment, physical plant, installed CAPEX, TIV | No dollar loss emitted | No approved denominator crosswalk | Valuation approval | Value crosswalk
Portfolio metrics | None | Scenario loss, EAL, PML, VaR, TVaR | Withhold | Partial cell coverage | Broader failure-unit coverage plus consumer QA | Capability contract
GSU rule: WT_GSU_SUBSTATION is a single facility-level exposure and is never multiplied by turbine count. The asset identity can be shared across solar and wind, but a flood-GSU curve or solar-GSU curve cannot be reused as tropical-cyclone wind response without pathway-matched evidence.

## Inputs
Source-native curve inputs
Editable yellow parameter cells reproduce the published fitted expected-damage equation; exact selectors are mandatory.
Curve ID | Archetype ID | Rated MW | Hub m | Rotor m | V_zero km/h | delta_V50 km/h | rho | Absolute D50 km/h | Core low km/h | Core high km/h | max_dr | Source limitation flag
TCWW_JAIMES_1MW_44M_SCREENING | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 1 | 44 | 50 | 90 | 106.77 | 8.94 | 196.77 | 108 | 252 | 1 | SOURCE_1MW_HUB_HEIGHT_TABLE_44M_FIGURE_CAPTION_40M
TCWW_JAIMES_2P5MW_80M_SCREENING | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 2.5 | 80 | 90 | 90 | 82.52 | 4.54 | 172.52 | 108 | 252 | 1
TCWW_JAIMES_3P3MW_100M_SCREENING | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 3.3 | 100 | 114 | 90 | 73.3 | 4.99 | 163.3 | 108 | 252 | 1
Contract input | Required value | Default | Failure behavior | Notes
pathway_id | tropical_cyclone_wind | none | reject | No convective-wind or tornado fallback
failure_unit_id | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | none | withhold other units | Source-native quarantined atom
source_model_assumption_set_id | JAIMES_2020_GENERIC_FIXED_BASE_STEEL_PARKED_ROTOR_AS_DOCUMENTED | none | reject | Acknowledgement, not protection credit
actual_operating_control_state | consistent / inconsistent / unknown | unknown | inconsistent withholds; unknown flags | No numeric modifier
artifact hazard_axis_id | TC_PEAK_GUST_3S_10M_KMH_JAIMES | artifact-pinned | consumer pin mismatch rejects | Verified against the artifact; not a duplicate request field
tc_peak_gust_3s_10m_kmh | finite numeric | none | range policy | No implicit unit, height, duration, or category bridge

## Jaimes_Curves
Jaimes source-family expected damage curves
Formula audit: DR=0 for V<=90; otherwise 1−EXP[−LN(2)×((V−90)/delta)^rho]. Runtime support still follows the range/status column.
Wind km/h | 1 MW / 44 m DR | 2.5 MW / 80 m DR | 3.3 MW / 100 m DR | Runtime domain | Interpretation
0 | 0 | 0 | 0 | SUPPORTED_SOURCE_ZERO | Zero only with non-empirical threshold flag
60 | 0 | 0 | 0 | SUPPORTED_SOURCE_ZERO | Zero only with non-empirical threshold flag
90 | 0 | 0 | 0 | SUPPORTED_SOURCE_ZERO | Zero only with non-empirical threshold flag
100 | 4.4309e-10 | 4.7823e-05 | 3.3416e-05 | WITHHOLD_GAP | Formula shown for audit only; runtime DR is null
108 | 8.4845e-08 | 0.00068934 | 0.00062752 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
120 | 8.1649e-06 | 0.0069864 | 0.0079992 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
140 | 0.00078544 | 0.068799 | 0.097655 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
150 | 0.0040021 | 0.15049 | 0.22526 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
160 | 0.015784 | 0.27992 | 0.42351 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
163.3 | 0.023731 | 0.33288 | 0.5 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
172.52 | 0.066923 | 0.5 | 0.71405 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
180 | 0.13969 | 0.64221 | 0.8549 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
196.77 | 0.5 | 0.89275 | 0.9892 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
200 | 0.59537 | 0.92239 | 0.99477 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
220 | 0.9822 | 0.99573 | 0.99999 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
240 | 1 | 0.99997 | 1 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
252 | 1 | 1 | 1 | SUPPORTED_CORE | Runtime scalar DR may be evaluated
260 | 1 | 1 | 1 | WITHHOLD_HIGH | Formula shown for audit only; runtime DR is null

## Failure_Units
Failure-unit coverage
Only one quarantined source-native atom has a conditional numeric screening curve. Every other row remains explicit null/withheld.
Failure unit | Subsystem | Component | Treatment | Coverage status | Denominator | Exposure grain | Reason codes
WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | REPEATED_TURBINE_SOURCE_NATIVE | TOWER_TRIGGERED_SINGLE_TURBINE_RECORD_JAIMES | primary_nonzero | conditional_numeric_screening_curve | Jaimes paper-defined per-turbine/turbine-tower replacement-cost proxy Ct(h); not CWER tower, standard turbine-equipment assembly, BOS, physical plant, or TIV | one modeled turbine point
WT_TURBINE_EQUIPMENT_ASSEMBLY | REPEATED_TURBINE | ROTOR_NACELLE_TOWER_DEPENDENCY_SAFE_ASSEMBLY | withheld | withheld_not_zero | same-unit turbine-equipment replacement value | as specified by standard unit | SOURCE_NATIVE_ATOM_NOT_HARMONIZED_TO_STANDARD_EQUIPMENT_ASSEMBLY; OMITTED_NON_TOWER_FAILURE_MODES
WT_FOUNDATION | FOUNDATION | TURBINE_FOUNDATION_OR_BASE | withheld | withheld_not_zero | same-unit foundation replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT
WT_PAD_MOUNTED_ELECTRICAL | PLANT_ELECTRICAL | PAD_TRANSFORMER_AND_SWITCHGEAR | withheld | withheld_not_zero | same-unit pad-electrical replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT; ELECTRICAL_VALUE_SPLIT_REQUIRED
WT_COLLECTION_SYSTEM | PLANT_ELECTRICAL | COLLECTION_CABLE_AND_POLES | withheld | withheld_not_zero | same-unit line/network replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT; LINE_NETWORK_EXPOSURE_REQUIRED
WT_GSU_SUBSTATION | SUBSTATION | GSU_TRANSFORMER_SWITCHYARD_AND_CONTROL | withheld | withheld_not_zero | same facility-level GSU/substation replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT; FACILITY_LEVEL_EXPOSURE_REQUIRED
WT_CONTROL_BUILDING_AND_SCADA | CONTROL | CONTROL_BUILDING_SCADA_AND_COMMUNICATIONS | withheld | withheld_not_zero | same-unit control and communications replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT
WT_CIVIL_INFRA | PLANT_CIVIL | ACCESS_ROADS_CRANE_PADS_BUILDINGS_AND_FENCES | withheld | withheld_not_zero | split direct civil replacement value | as specified by standard unit | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT; MIXED_CIVIL_BUCKET_REQUIRES_SPLIT
SUPPORT_FIELDWORK | SUPPORT | ASSEMBLY_INSTALLATION_AND_CRANE_SCOPE | withheld | withheld_not_zero | post-damage repair work scope | as specified by standard unit | SUPPORT_COST_ALLOCATE_ONCE_AFTER_DISPOSITION; NO_INDEPENDENT_FRAGILITY
SUPPORT_TRANSPORT_LOGISTICS | SUPPORT | TRANSPORT_AND_REPLACEMENT_LOGISTICS | withheld | withheld_not_zero | post-damage replacement logistics scope | as specified by standard unit | SUPPORT_COST_ALLOCATE_ONCE_AFTER_DISPOSITION; NO_INDEPENDENT_FRAGILITY

## Value_Crosswalk
value_source_id | source_location | row_or_bucket_id | row_or_bucket_label | value | unit | financial_class | failure_unit_id | applicable_pathway_ids | role_in_loss | include_in_direct_denominator | allocation_rule | double_count_guardrail | status | notes
JAIMES_CT_H | Jaimes 2020 §3.2 and Table 1 footnote | JAIMES_VALUE_1MW_HH44 | Source-native 1 MW/44 m turbine-tower exposure proxy | 1281322.3778 | source_nominal_USD_vintage_unspecified | source_replacement_proxy | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | tropical_cyclone_wind | source_denominator_audit | TRUE | Ct(h)=1307.9*h^1.82 at h=44 m; audit only; no runtime dollar emit. | Mutually exclusive with every CWER mapping and with WT_TURBINE_EQUIPMENT_ASSEMBLY. | source_native_audit_only | Paper wording mixes selected structure, turbine tower, and total turbine cost.
JAIMES_CT_H | Jaimes 2020 §3.2 and Table 1 footnote | JAIMES_VALUE_2P5MW_HH80 | Source-native 2.5 MW/80 m turbine-tower exposure proxy | 3803630.4554 | source_nominal_USD_vintage_unspecified | source_replacement_proxy | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | tropical_cyclone_wind | source_denominator_audit | TRUE | Ct(h)=1307.9*h^1.82 at h=80 m; audit only; no runtime dollar emit. | Mutually exclusive with every CWER mapping and with WT_TURBINE_EQUIPMENT_ASSEMBLY. | source_native_audit_only | Paper wording mixes selected structure, turbine tower, and total turbine cost.
JAIMES_CT_H | Jaimes 2020 §3.2 and Table 1 footnote | JAIMES_VALUE_3P3MW_HH100 | Source-native 3.3 MW/100 m turbine-tower exposure proxy | 5709190.5699 | source_nominal_USD_vintage_unspecified | source_replacement_proxy | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | tropical_cyclone_wind | source_denominator_audit | TRUE | Ct(h)=1307.9*h^1.82 at h=100 m; audit only; no runtime dollar emit. | Mutually exclusive with every CWER mapping and with WT_TURBINE_EQUIPMENT_ASSEMBLY. | source_native_audit_only | Paper wording mixes selected structure, turbine tower, and total turbine cost.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!2:9 | CWER_TURBINE_EQUIPMENT | Rotor, nacelle, yaw, power electronics, and tower equipment | 1090 | 2023_USD_per_kW | direct_hardware | WT_TURBINE_EQUIPMENT_ASSEMBLY | tropical_cyclone_wind | comparison_only | FALSE | No mapping until the source denominator and omitted failure modes are reconciled. | Do not multiply the Jaimes source-native DR by the 1090 USD/kW assembly. | withheld_crosswalk | Complete equipment bucket; Jaimes is tower-triggered and component-incomplete.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!9 | CWER_TOWER_MODULE | Tower module | 276 | 2023_USD_per_kW | direct_hardware | WT_TURBINE_EQUIPMENT_ASSEMBLY | tropical_cyclone_wind | comparison_only | FALSE | No tower-only mapping because the source economic consequence invokes total turbine cost. | Do not relabel the source-native atom as a tower-module DR. | withheld_crosswalk | Useful denominator sensitivity only.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!10 | CWER_FOUNDATION | Foundation | 120 | 2023_USD_per_kW | direct_hardware | WT_FOUNDATION | tropical_cyclone_wind | withheld_unit_value | FALSE | Separate same-unit curve required. | Unmodeled foundation damage is not zero and is not inherited from tower response. | withheld_no_curve | Per-turbine point value.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!12 | CWER_EXTERNAL_ELECTRICAL | Mixed external electrical | 72 | 2023_USD_per_kW | mixed_direct_hardware | WT_PAD_MOUNTED_ELECTRICAL;WT_COLLECTION_SYSTEM;WT_GSU_SUBSTATION;WT_CONTROL_BUILDING_AND_SCADA | tropical_cyclone_wind | split_required | FALSE | Split pad point, line/network, facility GSU, and control values before curves. | Do not repeat facility value by turbine or allocate the mixed row without a governed rule. | withheld_split_required | Asset-neutral identities do not supply pathway-specific response.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!11 | CWER_CIVIL | Site access, staging, and facilities | 47 | 2023_USD_per_kW | mixed_civil | WT_CIVIL_INFRA | tropical_cyclone_wind | split_required | FALSE | Split roads, crane pads, buildings, and fences. | Do not set mixed civil to zero from direct-wind intuition. | withheld_split_required | Line/network/polygon grains differ.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!13 | CWER_FIELDWORK_SUPPORT | Assembly and installation | 100 | 2023_USD_per_kW | replacement_support_cost | SUPPORT_FIELDWORK | all_shared | support_allocate_once | FALSE | Allocate once after disposition under a reviewed repair-scope rule. | Do not assign an independent wind fragility or add automatically to source consequence ratios. | withheld_support_rule | Potential overlap with source assumed rebuild ratios.
NREL_CWER_2024 | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Wind_Map!14 | CWER_TRANSPORT_SUPPORT | Wind turbine transport | 194 | 2023_USD_per_kW | replacement_support_cost | SUPPORT_TRANSPORT_LOGISTICS | all_shared | support_allocate_once | FALSE | Allocate once after replacement disposition and access/crane review. | Do not assign an independent wind fragility or add automatically to source consequence ratios. | withheld_support_rule | Potential overlap with source assumed rebuild ratios.
SUMMARY | Wind_Map!2:14 | CWER_PHYSICAL_REFERENCE | Physical replaceable reference basis | 1623 | 2023_USD_per_kW | reconciliation | REFERENCE_DENOMINATOR_ONLY | all_shared | comparison_only | FALSE | 1090 equipment + 239 other direct + 294 support. | Never apply Jaimes DR to the whole physical basis. | reconciled_not_runtime | Reference only.
SUMMARY | Wind_Map!2:19 | CWER_INSTALLED_REFERENCE | Installed reference basis | 1968 | 2023_USD_per_kW | reconciliation | REFERENCE_DENOMINATOR_ONLY | all_shared | comparison_only | FALSE | 1623 physical + 345 excluded soft/sunk/nonphysical. | Never apply Jaimes DR to installed CAPEX or TIV. | reconciled_not_runtime | Reference only.
|  |  |  | 0 | [5 empty] | FALSE

## Old_vs_New
comparison_id | wind_speed_kmh | wind_speed_mph_unit_conversion_only | turbine_archetype_id | v1_runtime_domain_status | v1_runtime_source_unit_dr | v1_formula_audit_dr | v0_1_runtime_source_unit_dr | hazard_placeholder_full_tiv_dr | legacy_memo_rotor_curve_dr | v1_failure_unit | v1_denominator | hazard_placeholder_endpoint_denominator | legacy_memo_axis_endpoint | axis_and_endpoint_comparability | comparison_disposition
TCWW-CMP-001 | 90 | 55.923407301 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_SOURCE_ASSUMED_NO_DAMAGE_THRESHOLD_NOT_EMPIRICAL | 0.000000000000000 | 0.000000000000000 |  | 0.000013808479213 | 0.009962596264405 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | v0.1 null is baseline; both old numerics are audit-only and not regression targets
TCWW-CMP-002 | 100 | 62.137119224 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | withheld_BELOW_SOURCE_SIMULATION_RANGE |  | 0.000000000443087 |  | 0.000030945222439 | 0.015713280326587 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes formula value is audit-only in 90-108 gap; old endpoints remain incomparable | withhold v1 runtime; do not use either old numeric as fallback
TCWW-CMP-003 | 108 | 67.108088762 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_source_range | 0.000000084844835 | 0.000000084844835 |  | 0.000059044662073 | 0.022564717366808 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | compare directionally only; do not calibrate v1 to old values
TCWW-CMP-004 | 196.77 | 122.267209497 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_source_range | 0.500000000000000 | 0.500000000000000 |  | 0.068349337178772 | 0.540762637165423 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Exact v1 midpoint; numerical closeness to legacy rotor is coincidental and not like-for-like | midpoint KAT for v1; old values audit-only
TCWW-CMP-005 | 180 | 111.846814603 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_source_range | 0.139686727984598 | 0.139686727984598 |  | 0.019456260060225 | 0.372556430596958 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | compare directionally only; do not calibrate v1 to old values
TCWW-CMP-006 | 220 | 136.701662292 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_source_range | 0.982198894878260 | 0.982198894878260 |  | 0.261216320978339 | 0.724675011768098 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | large delta is expected from different model/endpoint; not a regression failure
TCWW-CMP-007 | 252 | 156.585540444 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | supported_source_range | 0.999999999999693 | 0.999999999999693 |  | 0.563208912474459 | 0.839036165112190 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Upper supported v1 boundary; old caps/denominators are not comparable | boundary KAT; do not extend runtime from old curves
TCWW-CMP-008 | 253 | 157.206911636 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | withheld_ABOVE_SOURCE_SIMULATION_RANGE |  | 0.999999999999940 |  | 0.568613424466259 | 0.840804387591376 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes mathematical tail is audit-only above 252; old endpoints remain incomparable | withhold v1 runtime; do not clamp or use old fallback
TCWW-CMP-009 | 90 | 55.923407301 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_SOURCE_ASSUMED_NO_DAMAGE_THRESHOLD_NOT_EMPIRICAL | 0.000000000000000 | 0.000000000000000 |  | 0.000013808479213 | 0.009962596264405 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | v0.1 null is baseline; both old numerics are audit-only and not regression targets
TCWW-CMP-010 | 100 | 62.137119224 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | withheld_BELOW_SOURCE_SIMULATION_RANGE |  | 0.000047822934381 |  | 0.000030945222439 | 0.015713280326587 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes formula value is audit-only in 90-108 gap; old endpoints remain incomparable | withhold v1 runtime; do not use either old numeric as fallback
TCWW-CMP-011 | 108 | 67.108088762 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_source_range | 0.000689340900421 | 0.000689340900421 |  | 0.000059044662073 | 0.022564717366808 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | compare directionally only; do not calibrate v1 to old values
TCWW-CMP-012 | 172.52 | 107.198958085 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_source_range | 0.500000000000000 | 0.500000000000000 |  | 0.010782749447981 | 0.300880134115842 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Exact v1 midpoint; neither old value shares the v1 endpoint/denominator | midpoint KAT for v1; old values audit-only
TCWW-CMP-013 | 180 | 111.846814603 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_source_range | 0.642205900008322 | 0.642205900008322 |  | 0.019456260060225 | 0.372556430596958 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | large delta is expected from different model/endpoint; not a regression failure
TCWW-CMP-014 | 220 | 136.701662292 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_source_range | 0.995733421640076 | 0.995733421640076 |  | 0.261216320978339 | 0.724675011768098 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | large delta is expected from different model/endpoint; not a regression failure
TCWW-CMP-015 | 252 | 156.585540444 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | supported_source_range | 0.999999633725535 | 0.999999633725535 |  | 0.563208912474459 | 0.839036165112190 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Upper supported v1 boundary; old caps/denominators are not comparable | boundary KAT; do not extend runtime from old curves
TCWW-CMP-016 | 253 | 157.206911636 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | withheld_ABOVE_SOURCE_SIMULATION_RANGE |  | 0.999999759312657 |  | 0.568613424466259 | 0.840804387591376 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes mathematical tail is audit-only above 252; old endpoints remain incomparable | withhold v1 runtime; do not clamp or use old fallback
TCWW-CMP-017 | 90 | 55.923407301 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_SOURCE_ASSUMED_NO_DAMAGE_THRESHOLD_NOT_EMPIRICAL | 0.000000000000000 | 0.000000000000000 |  | 0.000013808479213 | 0.009962596264405 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | v0.1 null is baseline; both old numerics are audit-only and not regression targets
TCWW-CMP-018 | 100 | 62.137119224 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | withheld_BELOW_SOURCE_SIMULATION_RANGE |  | 0.000033415608294 |  | 0.000030945222439 | 0.015713280326587 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes formula value is audit-only in 90-108 gap; old endpoints remain incomparable | withhold v1 runtime; do not use either old numeric as fallback
TCWW-CMP-019 | 108 | 67.108088762 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_source_range | 0.000627523692330 | 0.000627523692330 |  | 0.000059044662073 | 0.022564717366808 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | compare directionally only; do not calibrate v1 to old values
TCWW-CMP-020 | 163.30 | 101.469915692 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_source_range | 0.500000000000000 | 0.500000000000000 |  | 0.005156307063616 | 0.222912433500562 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Exact v1 midpoint; neither old value shares the v1 endpoint/denominator | midpoint KAT for v1; old values audit-only
TCWW-CMP-021 | 180 | 111.846814603 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_source_range | 0.854896589996166 | 0.854896589996166 |  | 0.019456260060225 | 0.372556430596958 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | large delta is expected from different model/endpoint; not a regression failure
TCWW-CMP-022 | 220 | 136.701662292 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_source_range | 0.999994401418475 | 0.999994401418475 |  | 0.261216320978339 | 0.724675011768098 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Hazard intensity is unit-convertible but endpoint/denominator/coverage differ; legacy axis and endpoint differ | large delta is expected from different model/endpoint; not a regression failure
TCWW-CMP-023 | 252 | 156.585540444 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | supported_source_range | 1.000000000000000 | 1.000000000000000 |  | 0.563208912474459 | 0.839036165112190 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Upper supported v1 boundary; displayed one is rounding; old caps/denominators are not comparable | boundary KAT uses full evaluator precision; do not extend runtime from old curves
TCWW-CMP-024 | 253 | 157.206911636 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | withheld_ABOVE_SOURCE_SIMULATION_RANGE |  | 1.000000000000000 |  | 0.568613424466259 | 0.840804387591376 | WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT | paper-native expected repair/replacement ratio on ambiguous turbine-tower/total-turbine proxy | mixed full-TIV fixed-share rotor+nacelle+substation+electrical DR; tower+foundation+civil forced zero | one-minute 10 m mph ordinary-logistic rotor DR | Jaimes mathematical tail is audit-only above 252; displayed one is rounding; old endpoints remain incomparable | withhold v1 runtime; do not clamp or use old fallback

## KATs
Formula known-answer tests
Absolute tolerance 1e-12; computed cells reference Inputs so parameter edits visibly change test status.
Test ID | Archetype ID | V km/h | delta_V50 | rho | Expected DR | Computed DR | Absolute error | Tolerance | Status | Expected runtime status
TCWW_JAIMES_1MW_44M_SCREENING_V90 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 90 | 106.77 | 8.94 | 0 | 0 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V108 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 108 | 106.77 | 8.94 | 8.4845e-08 | 8.4845e-08 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V160 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 160 | 106.77 | 8.94 | 0.015784 | 0.015784 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V180 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 180 | 106.77 | 8.94 | 0.13969 | 0.13969 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V200 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 200 | 106.77 | 8.94 | 0.59537 | 0.59537 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V220 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 220 | 106.77 | 8.94 | 0.9822 | 0.9822 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_V252 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 252 | 106.77 | 8.94 | 1 | 1 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_1MW_44M_SCREENING_ABSOLUTE_D50 | TCWW_JAIMES_GENERIC_1MW_HH44_V1 | 196.77 | 106.77 | 8.94 | 0.5 | 0.5 | 6.6613e-16 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V90 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 90 | 82.52 | 4.54 | 0 | 0 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V108 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 108 | 82.52 | 4.54 | 0.00068934 | 0.00068934 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V160 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 160 | 82.52 | 4.54 | 0.27992 | 0.27992 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V180 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 180 | 82.52 | 4.54 | 0.64221 | 0.64221 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V200 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 200 | 82.52 | 4.54 | 0.92239 | 0.92239 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V220 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 220 | 82.52 | 4.54 | 0.99573 | 0.99573 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_V252 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 252 | 82.52 | 4.54 | 1 | 1 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_2P5MW_80M_SCREENING_ABSOLUTE_D50 | TCWW_JAIMES_GENERIC_2P5MW_HH80_V1 | 172.52 | 82.52 | 4.54 | 0.5 | 0.5 | 4.4409e-16 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V90 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 90 | 73.3 | 4.99 | 0 | 0 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V108 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 108 | 73.3 | 4.99 | 0.00062752 | 0.00062752 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V160 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 160 | 73.3 | 4.99 | 0.42351 | 0.42351 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V180 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 180 | 73.3 | 4.99 | 0.8549 | 0.8549 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V200 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 200 | 73.3 | 4.99 | 0.99477 | 0.99477 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V220 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 220 | 73.3 | 4.99 | 0.99999 | 0.99999 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_V252 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 252 | 73.3 | 4.99 | 1 | 1 | 0 | 1e-12 | PASS | supported
TCWW_JAIMES_3P3MW_100M_SCREENING_ABSOLUTE_D50 | TCWW_JAIMES_GENERIC_3P3MW_HH100_V1 | 163.3 | 73.3 | 4.99 | 0.5 | 0.5 | 4.4409e-16 | 1e-12 | PASS | supported
Contract and fail-closed fixtures — human-readable mirror of executable KAT JSON
Test ID | Representative input | Expected status | Expected error/reason/flag | Fixture class | Mirror status
TCWW1_MISSING_ARCHETYPE | common valid fields; omission or mutation is named by test ID | rejected | TURBINE_ARCHETYPE_REQUIRED | contract / fail-closed | PRESENT
TCWW1_UNKNOWN_ARCHETYPE | turbine_archetype_id="GENERIC_MODERN_5MW" | rejected | TURBINE_ARCHETYPE_UNSUPPORTED | contract / fail-closed | PRESENT
TCWW1_NEAREST_NEIGHBOR_PROHIBITED | turbine_archetype_id="TCWW_NEAREST_FROM_4MW" | rejected | TURBINE_ARCHETYPE_UNSUPPORTED | contract / fail-closed | PRESENT
TCWW1_MISSING_SOURCE_ASSUMPTION_ACK | common valid fields; omission or mutation is named by test ID | rejected | SOURCE_MODEL_ASSUMPTION_SET_REQUIRED | contract / fail-closed | PRESENT
TCWW1_WRONG_SOURCE_ASSUMPTION_ACK | source_model_assumption_set_id="HEALTHY_ACTIVE_YAW" | rejected | SOURCE_MODEL_ASSUMPTION_SET_UNSUPPORTED | contract / fail-closed | PRESENT
TCWW1_CATEGORY_NOT_AXIS | saffir_simpson_category=4 | rejected | TC_SOURCE_NATIVE_AXIS_REQUIRED | contract / fail-closed | PRESENT
TCWW1_NHC_1MIN_NOT_AXIS | nhc_maximum_sustained_surface_wind_mps=60 | rejected | TC_SOURCE_NATIVE_AXIS_REQUIRED | contract / fail-closed | PRESENT
TCWW1_HUB_WIND_NOT_AXIS | hub_height_3s_gust_mps=70 | rejected | TC_SOURCE_NATIVE_AXIS_REQUIRED | contract / fail-closed | PRESENT
TCWW1_MPS_NOT_IMPLICITLY_CONVERTED | tc_peak_gust_3s_10m_mps=50 | rejected | TC_SOURCE_NATIVE_AXIS_REQUIRED | contract / fail-closed | PRESENT
TCWW1_NEGATIVE_REJECTED | tc_peak_gust_3s_10m_kmh=-1 | rejected | AXIS_OUTSIDE_VALID_RANGE | contract / fail-closed | PRESENT
TCWW1_LOWER_GAP_WITHHELD | tc_peak_gust_3s_10m_kmh=100 | withheld | BELOW_SOURCE_SIMULATION_RANGE | contract / fail-closed | PRESENT
TCWW1_UPPER_EXTRAPOLATION_WITHHELD | tc_peak_gust_3s_10m_kmh=260 | withheld | ABOVE_SOURCE_SIMULATION_RANGE | contract / fail-closed | PRESENT
TCWW1_ZERO_BRANCH_FLAGGED | tc_peak_gust_3s_10m_kmh=80 | supported | SOURCE_ASSUMED_NO_DAMAGE_THRESHOLD_NOT_EMPIRICAL | contract / fail-closed | PRESENT
TCWW1_WRONG_PATHWAY | pathway_id="straight_line_convective" | rejected | PATHWAY_ID_UNKNOWN | contract / fail-closed | PRESENT
TCWW1_TORNADO_ROUTES_SEPARATELY | pathway_id="tornado_direct_hit" | rejected | PATHWAY_ID_UNKNOWN | contract / fail-closed | PRESENT
TCWW1_STANDARD_EQUIPMENT_UNIT_WITHHELD | failure_unit_id="WT_TURBINE_EQUIPMENT_ASSEMBLY" | withheld | SOURCE_NATIVE_ATOM_NOT_HARMONIZED_TO_STANDARD_EQUIPMENT_ASSEMBLY | contract / fail-closed | PRESENT
TCWW1_FOUNDATION_WITHHELD_NOT_ZERO | failure_unit_id="WT_FOUNDATION" | withheld | NO_RUNTIME_CURVE_FOR_PATHWAY_UNIT | contract / fail-closed | PRESENT
TCWW1_GSU_WITHHELD_FACILITY_GRAIN | failure_unit_id="WT_GSU_SUBSTATION"; asset_subject_grain="facility_point" | withheld | FACILITY_LEVEL_EXPOSURE_REQUIRED | contract / fail-closed | PRESENT
TCWW1_SCENARIO_LOSS_WITHHELD_WITH_CWER | value_basis_id="NREL_CWER_2024"; direct_replacement_value_usd=3597000 | supported | SOURCE_DENOMINATOR_CROSSWALK_NOT_APPROVED | contract / fail-closed | PRESENT
TCWW1_SOURCE_NATIVE_VALUE_STILL_NONCANONICAL | value_basis_id="JAIMES_CT_H_SOURCE_NATIVE_REPLACEMENT_PROXY"; direct_replacement_value_usd=5709190.569869134 | supported | NONCANONICAL_PROPOSAL_NO_SCENARIO_LOSS | contract / fail-closed | PRESENT
TCWW1_UNKNOWN_CONTROL_STATE_FLAG_ONLY | actual_operating_control_state="unknown" | supported | SOURCE_MODEL_CONTROL_STATE_UNKNOWN | contract / fail-closed | PRESENT
TCWW1_INCONSISTENT_CONTROL_STATE_WITHHELD | actual_operating_control_state="known_inconsistent_with_source_assumption" | withheld | SOURCE_MODEL_CONTROL_STATE_MISMATCH | contract / fail-closed | PRESENT
TCWW1_1MW_HEIGHT_DISCREPANCY_FLAG | turbine_archetype_id="TCWW_JAIMES_GENERIC_1MW_HH44_V1" | supported | SOURCE_1MW_HUB_HEIGHT_TABLE_44M_FIGURE_CAPTION_40M | contract / fail-closed | PRESENT

## Source_Register
source_id | citation | url | accessed_on | exact_locator | source_type | source_role | pathway_ids | evidence_tier | target_asset_match | target_failure_unit_match | measured_or_modeled_endpoint | permitted_inference | prohibited_inference | decision | status | notes
TCWW-S001 | NOAA/National Hurricane Center, Glossary of NHC Terms, Maximum Sustained Surface Wind. | https://www.nhc.noaa.gov/aboutgloss.shtml | 2026-07-28 | entry: Maximum Sustained Surface Wind | government glossary | axis_boundary | tropical_cyclone_wind | T2_public_lab_standard_or_physics | none | none | one-minute average wind at 10 m in unobstructed exposure | Identify an upstream NHC source object and prove it is not the runtime curve axis. | Treat NHC sustained wind or category as the Jaimes 3-second-gust input. | reject_direct_runtime_axis_use | reviewed | A named validated bridge would be a later model change.
TCWW-S002 | International Electrotechnical Commission, IEC 61400-1:2019+AMD1:2025 CSV, Wind energy generation systems - Part 1: Design requirements. | https://webstore.iec.ch/en/publication/26423 | 2026-07-28 | official product page; scope and technical-change summary | standard | selector_context | tropical_cyclone_wind | T2_public_lab_standard_or_physics | direct | partial | wind-turbine design requirements including TC/high-turbulence treatment | Carry design lineage as future selector context. | Treat a design value as a damage threshold or modern-fleet transfer rule. | adopt_context_only | reviewed | Licensed clauses are not reproduced.
TCWW-S003 | Rose, S.; Jaramillo, P.; Small, M. J.; Grossmann, I.; Apt, J. Quantifying the hurricane risk to offshore wind turbines. PNAS 109(9), 3247-3252 (2012). DOI 10.1073/pnas.1111769109. | https://pmc.ncbi.nlm.nih.gov/articles/PMC3295275/ | 2026-07-28 | Methods Eq. 5 and Table 1 | peer-reviewed paper | validation_only | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | adjacent offshore reference | tower buckling only | binary tower-buckling probability under aligned active-yaw and perpendicular non-yaw states | Demonstrate that yaw/control state can materially change structural response. | Use as onshore economic DR or convert its axis without a bridge. | retain_validation_only | reviewed | Not a component-complete or same-axis model.
TCWW-S005 | Jaimes, M. A.; García-Soto, A. D.; Martín del Campo, J. O.; Pozos-Estrada, A. Probabilistic risk assessment on wind turbine towers subjected to cyclone-induced wind loads. Wind Energy 23(3), 528-546 (2020). DOI 10.1002/we.2436. | https://doi.org/10.1002/we.2436 | 2026-07-28 | §§2.3.1-2.3.2 and 3.2-3.3.5; Tables 2-3; Figures 5-6; Eqs. 1 and 11-13 | peer-reviewed paper | runtime_curve_source | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | exact three generic land-based source archetypes | source-native turbine-tower exposure record | analytical mean expected repair/replacement DR versus 3-second peak gust at 10 m | Adopt Eq. 1 for the three exact source selectors as a noncanonical screening v1 proposal with T4 consequence flags. | Claim modern-fleet transfer, claims calibration, BOP coverage, empirically calibrated spread, or a clean CWER denominator. | adopt_screening_v1_proposal | reviewed | Structural response is T3; assumed 90 km/h threshold and DS consequences make the composite economic ordinate T4. Source wording mixes turbine tower and total turbine cost.
TCWW-S006 | Electric Power Research Institute. Tropical Cyclone and Tornado Risks to Wind Turbines. Report 3002004460 (2014). | https://restservice.epri.com/publicdownload/000000003002004460/0/Product | 2026-07-28 | pp. 3-8 to 3-9; pp. 4-1 to 4-2; pp. 6-1 to 6-2 | industry technical report | evidence_gap | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | partial | partial | sparse modern-turbine loss record; gust-versus-duration distinction; yaw/grid-loss and damage-function gaps | Support explicit screening and data-gap labels. | Supply a numerical DR or transfer rule. | adopt_boundary_only | reviewed | The report says modern utility-turbine TC records are too limited for a claims-based damage function.
TCWW-S007 | Kapoor, A. et al. Hurricane eyewall winds and structural response of wind turbines. Wind Energy Science 5, 89-104 (2020). DOI 10.5194/wes-5-89-2020. | https://www.nrel.gov/docs/fy20osti/76101.pdf | 2026-07-28 | sections 2-4; Table 7; Conclusions | peer-reviewed modeling paper | mechanism_and_axis_context | tropical_cyclone_wind | T2_public_lab_standard_or_physics | adjacent | partial | modeled DTU 10-MW turbine loads under idealized Category-5 eyewall fields including veer and rapid direction change | Support prohibition on universal NHC/hub/rotor conversion and simple control credits. | Calibrate Jaimes economic DR or BOP. | adopt_boundary_only | reviewed | The study isolates atmospheric effects using an onshore turbine version but an offshore hurricane field and no waves.
TCWW-S008 | Chen, X.; Xu, J. Z. Structural failure analysis of wind turbines impacted by super typhoon Usagi. Engineering Failure Analysis 60, 391-404 (2016). DOI 10.1016/j.engfailanal.2015.11.028. | https://www.sciencedirect.com/science/article/pii/S1350630715301552 | 2026-07-28 | Wind farm damage overview; Design wind speed; Conclusions | peer-reviewed field and structural case study | case_study_severity | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | field-observed tower collapse and blade fracture in one 25-turbine coastal farm plus structural analysis of stop position and direction change | Support material selector/quality and omitted-mode guardrails. | Fit a transferable DR or cost ratio. | adopt_with_limits | reviewed | Eight towers collapsed and eleven additional blades failed; not a claims- or field-calibrated curve.
TCWW-S009 | Chou, J.-S.; Tu, W.-T. Failure analysis and risk management of a collapsed large wind turbine tower. Engineering Failure Analysis 18(1), 295-313 (2011). DOI 10.1016/j.engfailanal.2010.09.008. | https://www.sciencedirect.com/science/article/pii/S1350630710001603 | 2026-07-28 | post-disaster inspection and failure analysis | peer-reviewed forensic paper | case_study_severity | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | post-disaster investigation of one Jangmi tower collapse | Support tower-specific construction/bolt-quality selector relevance. | Derive a generic wind threshold or economic curve. | adopt_with_limits | reviewed | Single case, not calibration.
TCWW-S010 | Stehly, T.; Duffy, P.; Mulas Hernando, D. Cost of Wind Energy Review: 2024 Edition. NREL/TP-5000-91775. | https://www.nrel.gov/docs/fy25osti/91775.pdf | 2026-07-28 | land-based reference capital-cost breakdown; governed Wind_Map rows 2-19 | public-lab technical report | value_comparison_only | all_shared | T2_public_lab_standard_or_physics | modern generic reference | component and plant value buckets | 2023 USD/kW reference value ledger | Compare source denominator with modern governed buckets and keep GSU/collection/civil/support separate. | Use any CWER bucket as the Jaimes runtime denominator before independent crosswalk approval. | withhold_runtime_crosswalk | reviewed | 1090 equipment; 276 tower; 1623 physical; 1968 installed USD/kW are comparison values only.
TCWW-S014 | Chen, X.; Li, C.; Xu, J. Failure investigation on a coastal wind farm damaged by super typhoon: A forensic engineering study. Journal of Wind Engineering and Industrial Aerodynamics 147, 132-142 (2015). DOI 10.1016/j.jweia.2015.10.007. | https://doi.org/10.1016/j.jweia.2015.10.007 | 2026-07-28 | pp. 132-136; Tables 1-2; event loss and component disposition records | peer-reviewed forensic paper | coverage_boundary | tropical_cyclone_wind | T3_engineering_proxy_or_adjacent_empirical | direct | partial | blade-only and tower-collapse damage plus farm direct-loss estimates | Prove omitted blade modes and terminal dependency are material. | Divide farm costs by a generic denominator or calibrate a source-native curve. | adopt_with_limits | reviewed | Supports why the Jaimes atom cannot be a complete turbine-equipment curve.
GOVERNANCE_CONTRACT | Damage Modeling foundations and standards: provenance, cell package, selectors/conditioners/exposure, value linkage, capability, versioning, and pathway separation. | docs/method/standards/00_index.md | 2026-07-28 | standards 02, 06-10, 17, 20-23 and contracts 20-21 | governance standard | governance | all_shared | T4_placeholder_or_expert_judgment | not applicable | all | withhold-not-caveat and exact pinning requirements | Define the noncanonical proposal boundary, source-native atom, and promotion gates. | Override primary evidence or authorize silent defaults. | adopt | reviewed | Repository-owned governance source.
HAZARD_CONSUMER_AUDIT | Hazard_modeling TC wind-farm M3 placeholder audit pinned in v0.1 legacy evidence record. | Hazard_modeling/Notebooks/hurricane/wind_farm/m3_damage/01_damage.py | 2026-07-28 | pinned commit/blob in v0.1 LEGACY_EVIDENCE_INGESTION | consumer code audit | legacy_regression | tropical_cyclone_wind | T4_placeholder_or_expert_judgment | consumer placeholder | none | hardcoded convective curves and full-TIV shares | Use as a negative regression fixture for future cutover. | Treat consumer placeholder as curve evidence or canonical runtime. | reject_runtime_retain_regression | reviewed | Exact commit and blob remain in the v0.1 legacy audit.

## Claim_Register
claim_id | pathway_id | claim_text | claim_type | source_ids | exact_locator | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
TCWW-C025 | tropical_cyclone_wind | Jaimes publishes a bounded mean expected repair/replacement damage-ratio function, not only DS3 collapse fragility. | direct_observation | TCWW-S005 | §2.3.2 Eq. 1 and §3.3.5 Figure 6 | T3_engineering_proxy_or_adjacent_empirical | runtime_curve_family | adopt_screening_proposal | Evaluate the exact source family within its governed envelope. | Call it empirical, claims-calibrated, or component-complete. | The full text explicitly defines the economic ordinate and fitted continuous functions. | Author correction or independent reproduction failure.
TCWW-C026 | tropical_cyclone_wind | Eq. 1 is DR=0 for V<=90 and otherwise 1-exp[-ln(2)*((V-90)/delta_V50)^rho]. | direct_observation | TCWW-S005 | §2.3.2 Eq. 1; §3.3.5 Figure 6 parameters | T3_engineering_proxy_or_adjacent_empirical | thresholded_weibull_expected_damage | adopt_screening_proposal | Implement the exact fitted equation. | Treat delta_V50 as an absolute 50%-damage wind or substitute a logistic. | The published equation and Figure 6 resolve the typography. | Author correction or equation-reproduction failure.
TCWW-C027 | tropical_cyclone_wind | Absolute DR=0.5 occurs at V_zero+delta_V50: 196.77, 172.52, and 163.30 km/h. | derived_calculation | TCWW-S005 | Eq. 1 evaluated with Figure 6 parameters | T3_engineering_proxy_or_adjacent_empirical | V_at_DR50_kmh | adopt | KAT the derived absolute half-damage winds. | Repeat the paper prose that V50 alone is the absolute wind. | Substitution into Eq. 1 produces exactly 0.5. | Equation or parameters change.
TCWW-C028 | tropical_cyclone_wind | The three exact selectors are 1 MW/44 m/50 m, 2.5 MW/80 m/90 m, and 3.3 MW/100 m/114 m. | direct_observation | TCWW-S005 | Table 2 | T3_engineering_proxy_or_adjacent_empirical | turbine_archetype_id | adopt_exact_only | Select only an explicitly named source archetype. | Interpolate, nearest-match, or transfer to modern turbines. | The source models are discrete generic templates, not a continuous fleet model. | Matched modern archetype evidence.
TCWW-C029 | tropical_cyclone_wind | The 1 MW hub height is 44 m in Table 2/body text but 40 m in figure captions. | direct_observation | TCWW-S005 | Table 2 and Figures 5-6 captions | T3_engineering_proxy_or_adjacent_empirical | source_height_discrepancy_flag | adopt_flag | Use tabulated 44 m while emitting the discrepancy flag. | Silently normalize the source to 40 m or present it as consistent. | The tabulated model geometry is the stronger parameter locator. | Author correction.
TCWW-C030 | tropical_cyclone_wind | The native x-axis is 3-second peak gust at 10 m in km/h. | direct_observation | TCWW-S005 | §2.3.1; Eq. 1 variable definition | T3_engineering_proxy_or_adjacent_empirical | tc_peak_gust_3s_10m_kmh | adopt_exact_only | Evaluate source-native input only. | Use NHC one-minute wind, category, hub wind, mph, knots, or m/s without a named bridge. | Height, averaging period, and unit are explicit. | Validated bridge approved as a later change.
TCWW-C031 | tropical_cyclone_wind | The source response simulations span 108-252 km/h; the source equation separately defines a zero branch at V<=90. | direct_observation | TCWW-S005 | §3.3.2 and Eq. 1 | T3_engineering_proxy_or_adjacent_empirical | runtime_range_policy | adopt_fail_closed | Support 108-252; return flagged source-assumed zero at V<=90; withhold 90<V<108 and V>252. | Silently extrapolate the fitted curve outside the simulated range. | The numerical evidence range and analytic branch must remain distinct. | Matched evidence expands the supported range.
TCWW-C032 | tropical_cyclone_wind | The 90 km/h zero-damage threshold is an author assumption tied to typical cut-out speed, not an empirical immunity boundary. | direct_observation | TCWW-S005 | §2.3.2 discussion after Eq. 1 | T4_placeholder_or_expert_judgment | V_zero_kmh | adopt_with_flag | Carry SOURCE_ASSUMED_NO_DAMAGE_THRESHOLD_NOT_EMPIRICAL. | Claim physical immunity below 90 km/h. | The paper labels the threshold as assumed. | Matched low-severity observations.
TCWW-C033 | tropical_cyclone_wind | DS loss ratios are source-author assumptions: 2/43/100%, 4/48/100%, and 5/50/100% for the three classes. | direct_observation | TCWW-S005 | §3.3.5 before Eqs. 12-13 | T4_placeholder_or_expert_judgment | damage_state_consequences | adopt_as_source_assumption | Explain the economic screening grade. | Call consequences claims-derived or inspection-calibrated. | The authors state matching wind-farm loss data were unavailable. | Matched disposition and same-unit cost data.
TCWW-C034 | tropical_cyclone_wind | Eq. 1 is a fitted continuous approximation and must not be replaced by the Eq. 12 state-mixture calculation. | governance_decision | TCWW-S005;GOVERNANCE_CONTRACT | §3.3.5 Eqs. 1 and 12-13; numerical reproduction | T4_placeholder_or_expert_judgment | runtime_equation_precedence | adopt | Pin one runtime interpretation: the published final Eq. 1 fit. | Mix KATs or ordinates from Eq. 12 into Eq. 1. | The two representations are not numerically identical. | Formal model redesign.
TCWW-C035 | tropical_cyclone_wind | The paper's denominator wording mixes selected structure, turbine tower, and total turbine cost. | direct_observation | TCWW-S005 | §2.3, §3.2 Table 1 footnote, §3.3.5 | T4_placeholder_or_expert_judgment | source_denominator_scope | quarantine | Publish scalar DR only on a source-native atom pending valuation review. | Map to CWER tower, equipment, physical plant, installed CAPEX, or TIV. | The source does not provide a clean modern component boundary. | Independent valuation crosswalk approval.
TCWW-C036 | tropical_cyclone_wind | The source-native value proxy is Ct(h)=1307.9*h^1.82 USD per turbine/turbine-tower exposure record. | direct_observation | TCWW-S005 | §3.2 and Table 1 footnote | T3_engineering_proxy_or_adjacent_empirical | JAIMES_CT_H_SOURCE_NATIVE_REPLACEMENT_PROXY | retain_audit_only | Reproduce source values for denominator review. | Treat the proxy as a modern site appraisal or known-vintage CWER value. | The paper supplies the formula but not a clean current value scope. | Valuation review or source clarification.
TCWW-C037 | tropical_cyclone_wind | Jaimes tower states omit independent blade and other turbine-component failure modes. | direct_observation | TCWW-S005;TCWW-S008;TCWW-S014 | Jaimes §3.3.3; Chen event damage records | T3_engineering_proxy_or_adjacent_empirical | partial_failure_unit_coverage | adopt_withholding | Quarantine the curve to WT_JAIMES_TURBINE_TOWER_EXPOSURE_UNIT. | Call it complete WT_TURBINE_EQUIPMENT_ASSEMBLY vulnerability. | Field cases show blade failure on surviving towers. | Component-complete matched evidence.
TCWW-C038 | tropical_cyclone_wind | Foundation, pad equipment, collection, GSU, controls, civil, and support are withheld rather than zero. | governance_decision | TCWW-S008;TCWW-S010;TCWW-S014;GOVERNANCE_CONTRACT | coverage and value crosswalk review | T4_placeholder_or_expert_judgment | failure_unit_coverage | adopt_fail_closed | Return null DR and reason codes for uncovered units. | Turn absent evidence into zero damage. | Coverage roles require explicit withheld states. | Unit-specific evidence and approved curves.
TCWW-C039 | tropical_cyclone_wind | GSU/substation is one facility-level exposure and cannot be repeated by turbine count. | governance_decision | TCWW-S010;GOVERNANCE_CONTRACT | value/exposure and shared-substrate standards | T4_placeholder_or_expert_judgment | WT_GSU_SUBSTATION_exposure | adopt | Preserve facility grain and a separate pathway-specific response. | Roll GSU into each turbine or inherit flood/solar ordinates. | Shared identity does not erase exposure or pathway differences. | Approved asset registry changes.
TCWW-C040 | tropical_cyclone_wind | The source model assumes generic fixed-base steel towers and documents an internally inconsistent parked/feathered rotor state with wind parallel to rotor and no yaw. | direct_observation | TCWW-S005 | §§3.3.1-3.3.2 | T3_engineering_proxy_or_adjacent_empirical | source_model_assumption_set_id | adopt_acknowledgement | Require an explicit source-state acknowledgement and grant no control credit. | Label the curve healthy-yaw, failed-yaw, or universally protected. | The modeled state is load-bearing and internally inconsistent. | Author clarification or state-specific calibration.
TCWW-C041 | tropical_cyclone_wind | NHC maximum sustained surface wind is a one-minute average at 10 m and is not interchangeable with the Jaimes 3-second-gust axis. | direct_observation | TCWW-S001;TCWW-S005 | NHC glossary and Jaimes §2.3.1 | T2_public_lab_standard_or_physics | axis_bridge_guardrail | adopt | Reject direct NHC input. | Apply a global gust factor. | Averaging-period mismatch is explicit. | Validated bridge approved.
TCWW-C042 | tropical_cyclone_wind | TC-spawned tornado, rain, debris, flood/surge/scour, lightning/fire, and BI remain separate pathways or stages. | governance_decision | TCWW-S006;TCWW-S007;GOVERNANCE_CONTRACT | scope and pathway standards | T4_placeholder_or_expert_judgment | pathway_partition | adopt | Preserve event_family_id while routing mechanisms separately. | Fold all hurricane consequences into this curve or add overlapping coastal wind loss. | Causal pathways and value charges differ. | Approved compound-event model.
TCWW-C043 | tropical_cyclone_wind | The model v1 proposal supports conditional scalar DR only; scenario, whole-plant, EAL, PML, VaR, and TVaR remain withheld. | governance_decision | GOVERNANCE_CONTRACT;HAZARD_CONSUMER_AUDIT | capability v3 and migration review | T4_placeholder_or_expert_judgment | partial_capability | adopt_fail_closed | Expose a narrow noncanonical screening seam for review. | Report partial output as full-asset or financial risk. | Selector, denominator, coverage, and consumer promotion gates remain open. | All promotion gates pass.

## Parameter_Tiers
parameter | pathway_id | curve_id | value | param_role | tier | source_ids | reasoning | status | update_trigger
TCWW1-P001 ¦ required pathway | tropical_cyclone_wind | all | tropical_cyclone_wind | axis_bridge | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT | Prevents convective/tornado fallback and compound double count. | REQUIRED_NO_DEFAULT | approved pathway redesign
TCWW1-P002 ¦ source-native input field | tropical_cyclone_wind | all | tc_peak_gust_3s_10m_kmh | axis_bridge | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Exact paper axis: 3-second peak gust at 10 m in km/h. | ADOPT_EXACT_ONLY | validated bridge approved
TCWW1-P003 ¦ supported simulation lower bound | tropical_cyclone_wind | all | 108 | boundary_or_cap | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Lowest time-history intensity simulated by the source. | ADOPT_FAIL_CLOSED | matched evidence below 108 km/h
TCWW1-P004 ¦ supported simulation upper bound | tropical_cyclone_wind | all | 252 | boundary_or_cap | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Highest time-history intensity simulated by the source. | ADOPT_FAIL_CLOSED | matched evidence above 252 km/h
TCWW1-P005 ¦ source-assumed zero threshold | tropical_cyclone_wind | all | 90 km/h | boundary_or_cap | T4_placeholder_or_expert_judgment | TCWW-S005 | Author assumption tied to typical cut-out speed; not empirical immunity. | ADOPT_WITH_FLAG | matched low-severity damage observations
TCWW1-P006 ¦ 1MW delta V50 | tropical_cyclone_wind | TCWW_JAIMES_1MW_44M_SCREENING | 106.77 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 parameter interpreted as excess above V_zero. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P007 ¦ 1MW rho | tropical_cyclone_wind | TCWW_JAIMES_1MW_44M_SCREENING | 8.94 | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 shape. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P008 ¦ 1MW absolute D50 | tropical_cyclone_wind | TCWW_JAIMES_1MW_44M_SCREENING | 196.77 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Derived as 90+106.77 and KAT-locked. | DERIVED_CHECK | source equation changes
TCWW1-P009 ¦ 2.5MW delta V50 | tropical_cyclone_wind | TCWW_JAIMES_2P5MW_80M_SCREENING | 82.52 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 parameter interpreted as excess above V_zero. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P010 ¦ 2.5MW rho | tropical_cyclone_wind | TCWW_JAIMES_2P5MW_80M_SCREENING | 4.54 | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 shape. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P011 ¦ 2.5MW absolute D50 | tropical_cyclone_wind | TCWW_JAIMES_2P5MW_80M_SCREENING | 172.52 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Derived as 90+82.52 and KAT-locked. | DERIVED_CHECK | source equation changes
TCWW1-P012 ¦ 3.3MW delta V50 | tropical_cyclone_wind | TCWW_JAIMES_3P3MW_100M_SCREENING | 73.30 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 parameter interpreted as excess above V_zero. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P013 ¦ 3.3MW rho | tropical_cyclone_wind | TCWW_JAIMES_3P3MW_100M_SCREENING | 4.99 | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Figure 6 fitted Eq. 1 shape. | ADOPT_SCREENING | author correction or independent reproduction failure
TCWW1-P014 ¦ 3.3MW absolute D50 | tropical_cyclone_wind | TCWW_JAIMES_3P3MW_100M_SCREENING | 163.30 km/h | curve_fit_shape | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Derived as 90+73.30 and KAT-locked. | DERIVED_CHECK | source equation changes
TCWW1-P015 ¦ maximum DR | tropical_cyclone_wind | all | 1.0 | boundary_or_cap | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Bounded asymptote of source Eq. 1; not the rejected legacy 0.65 full-TIV cap. | ADOPT | source equation changes
TCWW1-P016 ¦ economic state consequences | tropical_cyclone_wind | all | 1MW 2/43/100%; 2.5MW 4/48/100%; 3.3MW 5/50/100% | open_seam_placeholder | T4_placeholder_or_expert_judgment | TCWW-S005 | Author-assumed DS ratios underlying the fitted mean vulnerability. | ADOPT_SOURCE_ASSUMPTION | matched claims and same-unit cost calibration
TCWW1-P017 ¦ exact archetype selector | tropical_cyclone_wind | all | three named Jaimes selectors; no default/interpolation/nearest neighbor | selector_default | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005;GOVERNANCE_CONTRACT | Prevents unsupported modern-fleet transfer. | REQUIRED_NO_DEFAULT | matched archetype-specific evidence
TCWW1-P018 ¦ source assumption set | tropical_cyclone_wind | all | JAIMES_2020_GENERIC_FIXED_BASE_STEEL_PARKED_ROTOR_AS_DOCUMENTED | conditioner_adjustment | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Acknowledges source model; no numeric control credit. | REQUIRED_ACKNOWLEDGEMENT | author clarification or state-specific evidence
TCWW1-P019 ¦ source-native value proxy | tropical_cyclone_wind | all | Ct(h)=1307.9*h^1.82 USD | exposure_or_value | T3_engineering_proxy_or_adjacent_empirical | TCWW-S005 | Retained only to audit the ambiguous source denominator. | WITHHOLD_RUNTIME_LOSS | independent valuation crosswalk approval
TCWW1-P020 ¦ CWER turbine equipment comparison | all_shared | none | 1090 2023 USD/kW | exposure_or_value | T2_public_lab_standard_or_physics | TCWW-S010 | Modern reference comparison only; no source-native mapping. | WITHHOLD_RUNTIME_CROSSWALK | independent valuation crosswalk approval
TCWW1-P021 ¦ CWER tower comparison | all_shared | none | 276 2023 USD/kW | exposure_or_value | T2_public_lab_standard_or_physics | TCWW-S010 | Modern tower-module comparison only; source ordinate is not tower-only. | WITHHOLD_RUNTIME_CROSSWALK | independent valuation crosswalk approval
TCWW1-P022 ¦ curve intrinsic spread | tropical_cyclone_wind | all | not_carried | open_seam_placeholder | T4_placeholder_or_expert_judgment | TCWW-S005;GOVERNANCE_CONTRACT | Source Beta treatment is not carried until fully reproduced and reviewed; it is not empirical spread. | WITHHOLD | reviewed uncertainty release
TCWW1-P023 ¦ all uncovered units | tropical_cyclone_wind | none | withheld_not_zero | open_seam_placeholder | T4_placeholder_or_expert_judgment | TCWW-S008;TCWW-S010;TCWW-S014;GOVERNANCE_CONTRACT | Case and value evidence show omitted modes and exposure grains are material. | ADOPT_FAIL_CLOSED | unit-specific curves and values
TCWW1-P024 ¦ scenario and annual metrics | all_shared | none | withheld | open_seam_placeholder | T4_placeholder_or_expert_judgment | GOVERNANCE_CONTRACT;HAZARD_CONSUMER_AUDIT | Partial noncanonical scalar DR cannot become full-asset financial risk. | ADOPT_FAIL_CLOSED | canonical promotion plus complete prerequisites

## QA
Workbook QA
These formula checks complement the repository validator, JSON schema checks, source review, and visual render inspection.
Check | Status | Expected | Workbook evidence | Meaning
Three curve records | PASS | 3 | README / Inputs | All exact Jaimes archetypes are present
Every KAT passes | PASS | 24 | KATs | Published equation reproduced
D50 identities hold | PASS | 3 | Inputs | V_at_DR50 = V_zero + delta_V50
Curves bounded | PASS | TRUE | Jaimes_Curves | Audit values remain in [0,1]
Curves monotonic | PASS | TRUE | Jaimes_Curves | Damage does not decline with intensity
One numeric failure unit | PASS | 1 | Failure_Units | Partial coverage is explicit
Nine withheld units | PASS | 9 | Failure_Units | Uncovered plant units are null, not zero
Source register rows | PASS | 12 | Source_Register | Evidence register copied into workbook
Claim register rows | PASS | 20 | Claim_Register | Claims and prohibitions preserved
Parameter rows | PASS | 25 | Parameter_Tiers | Every governed parameter/rule is tiered
Canonical flag false | PASS | FALSE | README | Proposal cannot silently cut over
Scenario loss withheld | PASS | WITHHELD | README | Partial DR cannot become whole-plant loss
Selector tuples unique | PASS | TRUE | Inputs | No duplicate or implicit selector route
1 MW discrepancy flagged | PASS | SOURCE_1MW_HUB_HEIGHT_TABLE_44M_FIGURE_CAPTION_40M | Inputs | 44 m choice preserves the 40/44 m source conflict
Gap and upper range withheld | PASS | 2 | Jaimes_Curves | Audit ordinates do not become runtime values
Physical value reconciles | PASS | 1623 | Value_Crosswalk | 1090 + 120 + 72 + 47 + 100 + 194
Installed value reconciles | PASS | 1968 | Value_Crosswalk | Physical 1623 plus excluded 345
Only source-native denominator rows included | PASS | 3 | Value_Crosswalk | No CWER row binds the Jaimes DR
Contract KAT mirror rows | PASS | 23 | KATs | Negative and fail-closed fixtures remain visible
Old-versus-new comparison rows | PASS | 24 | Old_vs_New | Baseline and legacy differences remain governed