## README
Wildfire × wind — model-v1 partial electrical screening
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
Identity | Value | Meaning
Damage code | WILDFIRE_WIND_PARTIAL_ELECTRICAL_SCREENING_V1 | two named unit DRs only
Model | model v1.0 | behavior-changing proposal
Canonical | FALSE | do not cut over Hazard
Supported units | WT_PAD_ELECTRICAL, WT_GSU_PROTECTION_CONTROL_DC | not a whole-farm curve
Axis | exact FSim class state 0..6 | screening ordinal, not local heat flux
Ordinate grade | Tier 4 | owner-authorized assumptions
Scenario dollars | withheld | site values and exposure split absent
Annual/tail metrics | withheld | downstream and prerequisites unmet
Guardrail: these curves make two real physical risks visible for screening. They do not prove a wind-farm loss calibration, do not value the farm, and do not turn every unmodeled subsystem into zero.

## Curves
Exact categorical screening state tables
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
Failure unit | Curve ID | Class state | DR | Tier | Interpretation
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 0 | 0 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 1 | 0.001 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 2 | 0.006 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 3 | 0.03 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 4 | 0.12 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 5 | 0.35 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_PAD_ELECTRICAL | WWV1_PAD_ELECTRICAL_FSIM_T4 | 6 | 0.7 | T4 | Lower T4 response than exposed controls because common apparatus has a steel exterior; polymeric, cable, seal, and auxiliary contents keep risk nonzero.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 0 | 0 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 1 | 0.004 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 2 | 0.02 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 3 | 0.08 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 4 | 0.25 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 5 | 0.6 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.
WT_GSU_PROTECTION_CONTROL_DC | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | 6 | 0.9 | T4 | Higher T4 response reflects polymeric, electronic, communications, battery, and cable content plus fire/heat replacement guidance; it is not a measured probability curve.

## KATs
Known-answer tests
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
Test ID | Failure unit | State | Expected DR | Status
wt_pad_electrical_state_0 | WT_PAD_ELECTRICAL | 0 | 0 | conditional
wt_pad_electrical_state_1 | WT_PAD_ELECTRICAL | 1 | 0.001 | conditional
wt_pad_electrical_state_2 | WT_PAD_ELECTRICAL | 2 | 0.006 | conditional
wt_pad_electrical_state_3 | WT_PAD_ELECTRICAL | 3 | 0.03 | conditional
wt_pad_electrical_state_4 | WT_PAD_ELECTRICAL | 4 | 0.12 | conditional
wt_pad_electrical_state_5 | WT_PAD_ELECTRICAL | 5 | 0.35 | conditional
wt_pad_electrical_state_6 | WT_PAD_ELECTRICAL | 6 | 0.7 | conditional
wt_gsu_protection_control_dc_state_0 | WT_GSU_PROTECTION_CONTROL_DC | 0 | 0 | conditional
wt_gsu_protection_control_dc_state_1 | WT_GSU_PROTECTION_CONTROL_DC | 1 | 0.004 | conditional
wt_gsu_protection_control_dc_state_2 | WT_GSU_PROTECTION_CONTROL_DC | 2 | 0.02 | conditional
wt_gsu_protection_control_dc_state_3 | WT_GSU_PROTECTION_CONTROL_DC | 3 | 0.08 | conditional
wt_gsu_protection_control_dc_state_4 | WT_GSU_PROTECTION_CONTROL_DC | 4 | 0.25 | conditional
wt_gsu_protection_control_dc_state_5 | WT_GSU_PROTECTION_CONTROL_DC | 5 | 0.6 | conditional
wt_gsu_protection_control_dc_state_6 | WT_GSU_PROTECTION_CONTROL_DC | 6 | 0.9 | conditional

## Sources
SOURCE_REGISTER_wildfire_wind__model_v1_0__docs_r1
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
source_id | citation | url | accessed_on | exact_locator | source_type | source_role | evidence_tier | permitted_inference | prohibited_inference | decision | notes
WW1-S001 | Dillon et al. Spatial datasets of probabilistic wildfire risk components for the United States (270 m), 3rd ed., USFS RDS-2016-0034-3 (2023). | https://www.fs.usda.gov/rds/archive/products/RDS-2016-0034-3/_metadata_RDS-2016-0034-3.html | 2026-08-08 | conditional flame-length probability class definitions and 270 m support | official hazard dataset metadata | axis_semantics | T2_public_lab_standard_or_physics | Preserve exact product and six source-native conditional classes. | Infer local equipment heat flux, duration, ignition probability, or economic DR. | adopt_with_limits | Burn probability remains a Hazard frequency input.
WW1-S002 | Severino et al. Assessing wildfire risk to critical infrastructure in central Chile: application to an electrical substation. International Journal of Wildland Fire (2024). DOI 10.1071/WF22113. | https://doi.org/10.1071/WF22113 | 2026-08-08 | substation target inventory; PMMA proxy-fuel radiant-flux probit; case heat-flux results | peer-reviewed primary modeling study | mechanism_and_ordering | T3_engineering_proxy_or_adjacent_empirical | Support nonzero vulnerability of polymeric substation contents and nonlinear ignition sensitivity to local radiant heat. | Transfer site frequency, PMMA ignition probability, local heat flux, or economic DR to a wind farm or FSim class. | adopt_with_limits | Pressure-test anchor, not numerical calibration.
WW1-S003 | NEMA GD 2-2016, Evaluating Fire- and Heat-Damaged Electrical Equipment. | https://www.nema.org/docs/default-source/standards-document-library/nema-gd-2-2016-evaluating-fire-and-heat-damaged-electrical-equipment-guide.pdf | 2026-08-08 | sections on switchgear, transformers, wire/cable, protective relays/meters, communications, UPS and residue | industry consensus guidance | post_fire_disposition | T2_public_lab_standard_or_physics | Support replacement-prone endpoints for damaged electronic, relay, communications, UPS, and cable items and qualified review of apparatus. | Infer pre-event wildfire fragility, FSim-class DR, or generic smoke loss. | adopt_with_limits | Disposition evidence only.
WW1-S004 | Butler, Wallace, and Hogge. Wildfire vulnerability of power transmission and distribution infrastructure (USFS, 2015). | https://research.fs.usda.gov/treesearch/49452 | 2026-08-08 | preliminary steel-tower and transformer/junction-enclosure simulations | official preliminary engineering study | negative_and_ordering_evidence | T3_engineering_proxy_or_adjacent_empirical | Keep common steel-enclosed apparatus below exposed polymeric/electronic contents in a screening ordering. | Assign immunity, a universal zero, or a numeric wind-farm DR. | adopt_with_limits | Preliminary and not wind-farm calibrated.
WW1-S005 | Damage Modeling wildfire_solar model v1.0/docs r3. | docs/cells/wildfire_solar/current/wildfire_solar__model_v1_0__docs_r3__curve_artifact.json | 2026-08-08 | WSV1_MV_EQUIPMENT_THERMAL and WSV1_SCADA_THERMAL point arrays | neighboring governed model | audit_comparison_only | T4_placeholder_or_expert_judgment | Record numerical identity after independent cell-local adoption as an audit fingerprint. | Claim evidence transfer, shared runtime dependency, or solar-to-wind calibration. | audit_only | Not included in source_parameter_refs as scientific evidence.
WW1-A001 | Owner direction in Damage Modeling task, 2026-08-08: represent wildfire-wind risk even if only one or two subsystems can be supported. | conversation_record | 2026-08-08 | explicit coverage-first Tier-4 business decision | owner assumption authorization | ordinate_adoption_authority | T4_placeholder_or_expert_judgment | Create a visibly labeled noncanonical two-unit screening proposal. | Relabel assumptions as empirical calibration or authorize canonical cutover. | adopt | Assumption set WW_T4_PARTIAL_ELECTRICAL_SCREENING_2026_08_08.
GOVERNANCE_CONTRACT | Damage Modeling governed damage-curve standards and skill workflow. | docs/method/standards/00_index.md | 2026-08-08 | cell package, provenance, pathway, capability, versioning, and fail-closed standards | internal governance control | governance | T4_placeholder_or_expert_judgment | Control package structure, labels, tests, and release state. | Serve as scientific calibration. | adopt | Governance only.

## Claims
CLAIM_PARAMETER_REGISTER_wildfire_wind__model_v1_0__docs_r1
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
claim_id | claim_text | claim_type | source_ids | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
WW1-C001 | FSim conditional flame-length class is a screening ordinal and not a local equipment heat-flux history. | source_semantics | WW1-S001 | T2_public_lab_standard_or_physics | axis_guardrail | adopt | Select an exact categorical screening state. | Convert class to kW/m2, duration, or ignition probability. | The source product does not carry the component-demand bridge. | Validated local-attack adapter.
WW1-C002 | Two named electrical failure units may emit conditional screening DR; all other wind-farm units remain withheld-not-zero. | governance_decision | WW1-A001;GOVERNANCE_CONTRACT | T4_placeholder_or_expert_judgment | partial_coverage | adopt | Report risk for the two named units only. | Report whole-farm DR or zero for missing units. | Partial honest coverage is more useful than an unqualified aggregate. | Additional failure-unit calibration or owner decision.
WW1-C003 | Pad electrical response is screened below protection-control-DC response. | engineering_ordering | WW1-S002;WW1-S003;WW1-S004 | T3_engineering_proxy_or_adjacent_empirical | relative_vulnerability_order | adopt_with_limits | Pressure-test the ordinal ordering. | Claim the numeric gap is measured. | Steel enclosure offers relative resistance while polymeric/electronic/cable contents are replacement-prone after fire/heat damage. | Wind-site inspection and claims evidence.
WW1-C004 | Both point arrays are Tier-4 cell-local assumptions. | assumption | WW1-A001 | T4_placeholder_or_expert_judgment | curve_ordinates | adopt_for_noncanonical_screening | Use for sensitivity and interface testing with exact acknowledgement. | Call the arrays wildfire-wind calibration, claims experience, or standard curves. | No public matched demand-to-disposition-to-cost dataset was found. | Structured elicitation or qualified empirical calibration.
WW1-C005 | Numerical identity to two wildfire-solar profiles is an audit fingerprint only. | cross_cell_boundary | WW1-S005;WW1-A001 | T4_placeholder_or_expert_judgment | no_shared_runtime_dependency | adopt | Detect drift and explain lineage. | Use the solar package as evidence or runtime fallback. | The wind cell independently owns the assumptions and failure-unit binding. | Independent wind calibration replaces the arrays.
WW1-C006 | Scenario dollars, whole-plant DR, EAL, PML, VaR, and TVaR remain withheld. | capability_boundary | GOVERNANCE_CONTRACT | T4_placeholder_or_expert_judgment | capability | adopt | Emit unit DR only. | Bind mixed electrical USD/kW or full TIV by default. | Site splits, exposure, frequency, aggregation, and canonical promotion are absent. | All recorded gates pass.

## Tiers
PARAMETER_TIER_TABLE_wildfire_wind__model_v1_0__docs_r1
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
parameter_id | curve_id | parameter | value | role | tier | source_ids | status | update_trigger
WW1-P001 | all | FSim class semantics | states 1..6; state 0 no-event control | axis | T2_public_lab_standard_or_physics | WW1-S001 | adopt_with_limits | source product change
WW1-P002 | WWV1_PAD_ELECTRICAL_FSIM_T4 | point array | [[0, 0.0], [1, 0.001], [2, 0.006], [3, 0.03], [4, 0.12], [5, 0.35], [6, 0.7]] | shape_and_level | T4_placeholder_or_expert_judgment | WW1-A001 | adopt_noncanonical_screening | qualified calibration or elicitation
WW1-P003 | WWV1_GSU_PROTECTION_CONTROL_DC_FSIM_T4 | point array | [[0, 0.0], [1, 0.004], [2, 0.02], [3, 0.08], [4, 0.25], [5, 0.6], [6, 0.9]] | shape_and_level | T4_placeholder_or_expert_judgment | WW1-A001 | adopt_noncanonical_screening | qualified calibration or elicitation
WW1-P004 | all | exact integer handling | reject noninteger/unknown/out-of-range | boundary | T4_placeholder_or_expert_judgment | WW1-A001;GOVERNANCE_CONTRACT | adopt | continuous local-demand bridge
WW1-P005 | all | intrinsic spread | not_carried | uncertainty | T4_placeholder_or_expert_judgment | WW1-A001 | withheld | structured uncertainty elicitation or empirical residuals

## Values
VALUE_CROSSWALK_wildfire_wind__model_v1_0__docs_r1
Noncanonical Tier-4 partial screening proposal • independent review and promotion blocked
failure_unit_id | spatial_grain | curve_denominator | available_reference_value | scenario_loss_status | required_site_fields | double_count_guardrail | notes
WT_PAD_ELECTRICAL | one turbine/pad point or small footprint | direct replacement value of the same exposed pad-electrical failure unit | none; mixed NREL 72 USD/kW row prohibited | withheld | unit count; construction; ownership; same-unit SOV; local class; exposure fraction | Do not also charge collection or aggregate electrical value. | DR is usable without dollars as a unit-level screening indicator.
WT_GSU_PROTECTION_CONTROL_DC | one shared GSU control building/room/cabinet package | direct replacement value of the same GSU protection-control-DC package | none; mixed NREL 72 USD/kW row prohibited | withheld | exact inventory; project ownership; same-unit SOV; local class; exposure fraction | Value the physical shared package once across wind, solar, or hybrid hosts. | Main transformer, switchgear, and cable terminations remain separate and withheld.
FULL_WIND_FARM | lease/project polygon | prohibited | full TIV prohibited | withheld | not applicable | No aggregate alias or default value shares. | Two-unit coverage must not be presented as total farm damage.