## README
STRONG WIND × SOLAR — PROPOSED MODEL v2.0
Noncanonical straight-line-convective screening package · docs r1 · current v1.0/docs r3 remains runtime
Field | Governed statement
Status | PROPOSED / NONCANONICAL / PROMOTION BLOCKED
Pathway | straight_line_convective: downburst, microburst, macroburst, gust front, local non-tornadic derecho outflow
Architectures | Rigid fixed tilt; exact-system-qualified 1P/2P single-axis tracker
Fixed axis | Qualified event/design net-pressure-demand ratio; T4 record medians carry capacity; flagged V² proxy only with named bridges
Tracker axis | tracker-normal local 3-second gust / exact-system critical-instability 3-second gust
Numeric grade | Broad T4 unweighted screening scenarios; not fitted, claims-calibrated, or probabilistic percentiles
Active units | Architecture-specific module field and above-ground structure
Withheld | Foundation, inverter/electrical, SCADA, civil, full-plant DR and all annual financial metrics
Dependency | Terminal structural replacement forces colocated module terminal exactly once
Value | Explicit site values required; NLR Q1-2025 2024 USD reference is informational only
Current invariant | strong_wind_solar@model_v1_0__docs_r3; SHA 832f47d… remains canonical

## Scope_Pathway
Scope and pathway boundary
Exact causal routing is required; neighboring hazards receive no numeric fallback
Hazard/event | Status | Route | Rule
downburst / microburst / macroburst | in scope | Local non-tornadic convective outflow | Require site-local demand and parent event ID
gust front / thunderstorm outflow | in scope | Straight-line convective | Same local-demand rule
derecho | conditional | Parent convective event | Resolve local non-tornadic mechanism; partition embedded tornadoes
tropical cyclone / hurricane | out | Future hurricane_wind_solar | Duration/profile/rain/debris/control differ
tornado | out | Future tornado_solar | Rotating flow/debris/swath exposure differ
synoptic / downslope | out | Separate workstream | Stationarity/profile/duration differ
hail | out | hail_solar | Reconcile shared module disposition after separate evaluation
debris / rain ingress / lightning / flood | out | Separate mechanism | Not aerodynamic pressure DR
lifetime fatigue / downtime / BI | out | Reliability or downstream consumer | Not occurrence physical destruction

## Architecture_Axes
Architecture-specific demand axes
Fixed tilt and trackers share a convective pathway but not a normalization
Architecture | Axis | Required inputs | Valid range | Flags | Prohibited shortcut
fixed_tilt_ground_mount_screening_v1 | q_event_net / q_design_demand | event/design pressure ratio + aerodynamic bridge ID | 0–2 | below .2; above 1.6 | design demand treated as resistance; raw 10 m wind or design speed treated as D50
fixed speed proxy | (Varray/Vdesign)^2 | array-height gust + design gust + profile and demand bridge IDs | 0–2 | QUASI_STEADY_GUST_PROXY_USED | ordinary default power law
single_axis_tracker_qualified_screening_v1 | Vnormal_3s / Ucrit_3s | local normal gust + positive Ucrit + qualification ID + profile bridge + 1P/2P | 0–2 | stow action ≥.75; high >1.7 | generic Ucrit, fixed-tilt coefficients, universal stow multiplier
FM 0.75 Ucrit is an operational stow-action flag only. It is not damage onset and does not force zero below it.

## Curve_Records
Curve records and independent equation audit
Edit sample x in column M; columns N–U calculate exceedance, exact states and expected DR
Architecture | Failure unit | Curve ID | beta_ln | zero below | DS1 cost | DS2 cost | DS3 cost | Scenario | theta1 | theta2 | theta3 | sample x | Q1 | Q2 | Q3 | P0 | P1 | P2 | P3 | DR
fixed | PV_FIXED_TILT_MODULE_FIELD | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | 0.3 | 0.1 | 0.1 | 1 | 0 | lower_resistance | 0.65 | 1.2 |  | 1 | 0.92449 | 0.27168 | 0 | 0.075509 | 0.65281 | 0.27168 | 0 | 0.33696
fixed | PV_FIXED_TILT_MODULE_FIELD | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | 0.3 | 0.1 | 0.1 | 1 | 0 | central_screening | 0.85 | 1.55 |  | 1 | 0.706 | 0.072028 | 0 | 0.294 | 0.63397 | 0.072028 | 0 | 0.13543
fixed | PV_FIXED_TILT_MODULE_FIELD | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | 0.3 | 0.1 | 0.1 | 1 | 0 | upper_resistance | 1.05 | 1.95 |  | 1 | 0.4354 | 0.013004 | 0 | 0.5646 | 0.4224 | 0.013004 | 0 | 0.055244
fixed | PV_FIXED_TILT_SUPPORT_STRUCTURE | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | 0.3 | 0.1 | 0.15 | 1 | 1 | lower_resistance | 0.9 | 1.2 | 1.5 | 1 | 0.63728 | 0.27168 | 0.08826 | 0.36272 | 0.3656 | 0.18342 | 0.08826 | 0.32652
fixed | PV_FIXED_TILT_SUPPORT_STRUCTURE | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | 0.3 | 0.1 | 0.15 | 1 | 1 | central_screening | 1.15 | 1.55 | 1.9 | 1 | 0.32065 | 0.072028 | 0.016197 | 0.67935 | 0.24862 | 0.055831 | 0.016197 | 0.10932
fixed | PV_FIXED_TILT_SUPPORT_STRUCTURE | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | 0.3 | 0.1 | 0.15 | 1 | 1 | upper_resistance | 1.45 | 1.95 | 2.35 | 1 | 0.10776 | 0.013004 | 0.0021994 | 0.89224 | 0.094753 | 0.010804 | 0.0021994 | 0.027217
tracker | PV_TRACKER_MODULE_FIELD | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.275 | 0.1 | 0.1 | 1 | 0 | lower_resistance | 0.8 | 1.15 |  | 1 | 0.79144 | 0.30565 | 0 | 0.20856 | 0.48579 | 0.30565 | 0 | 0.35423
tracker | PV_TRACKER_MODULE_FIELD | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.275 | 0.1 | 0.1 | 1 | 0 | central_screening | 0.95 | 1.4 |  | 1 | 0.57398 | 0.11056 | 0 | 0.42602 | 0.46342 | 0.11056 | 0 | 0.15691
tracker | PV_TRACKER_MODULE_FIELD | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.275 | 0.1 | 0.1 | 1 | 0 | upper_resistance | 1.1 | 1.7 |  | 1 | 0.36445 | 0.026831 | 0 | 0.63555 | 0.33762 | 0.026831 | 0 | 0.060593
tracker | PV_TRACKER_SBOS_ASSEMBLY | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 0.275 | 0.1 | 0.15 | 1 | 1 | lower_resistance | 0.95 | 1.15 | 1.35 | 1 | 0.57398 | 0.30565 | 0.13757 | 0.42602 | 0.26833 | 0.16807 | 0.13757 | 0.3459
tracker | PV_TRACKER_SBOS_ASSEMBLY | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 0.275 | 0.1 | 0.15 | 1 | 1 | central_screening | 1.15 | 1.4 | 1.65 | 1 | 0.30565 | 0.11056 | 0.034303 | 0.69435 | 0.19508 | 0.07626 | 0.034303 | 0.13983
tracker | PV_TRACKER_SBOS_ASSEMBLY | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 0.275 | 0.1 | 0.15 | 1 | 1 | upper_resistance | 1.35 | 1.7 | 2 | 1 | 0.13757 | 0.026831 | 0.0058588 | 0.86243 | 0.11074 | 0.020972 | 0.0058588 | 0.043442

## Curve_Data
Central screening curve data
Formula-backed values from the governed parameters; scenarios remain unweighted
Demand index | Fixed module | Fixed structure | Tracker module | Tracker SBOS
0 | 0 | 0 | 0 | 0
0.05 | 0 | 0 | 0 | 0
0.1 | 4.8905e-14 | 3.3307e-17 | 1.1102e-17 | 0
0.15 | 3.6908e-10 | 8.4627e-13 | 9.5943e-13 | 9.8893e-15
0.2 | 7.0689e-08 | 4.1777e-10 | 7.316e-10 | 1.5691e-11
0.25 | 2.2596e-06 | 2.7809e-08 | 6.0499e-08 | 2.31e-09
0.3 | 2.5897e-05 | 5.8084e-07 | 1.3948e-06 | 8.6084e-08
0.35 | 0.0001553 | 5.7974e-06 | 1.4324e-05 | 1.3368e-06
0.4 | 0.00060212 | 3.5034e-05 | 8.5269e-05 | 1.1441e-05
0.45 | 0.0017173 | 0.00014812 | 0.00034576 | 6.3992e-05
0.5 | 0.0039198 | 0.00048129 | 0.0010612 | 0.00026112
0.55 | 0.007587 | 0.001281 | 0.0026498 | 0.00083762
0.6 | 0.012983 | 0.0029206 | 0.0056639 | 0.002226
0.65 | 0.020257 | 0.0058919 | 0.010752 | 0.005091
0.7 | 0.0295 | 0.010771 | 0.018613 | 0.010308
0.75 | 0.040814 | 0.018166 | 0.029954 | 0.01888
0.8 | 0.054358 | 0.028658 | 0.045436 | 0.031809
0.85 | 0.07035 | 0.042743 | 0.065613 | 0.049955
0.9 | 0.089045 | 0.060782 | 0.090864 | 0.07391
0.95 | 0.11068 | 0.082971 | 0.12134 | 0.10391
1 | 0.13543 | 0.10932 | 0.15691 | 0.13983
1.05 | 0.16334 | 0.13967 | 0.19718 | 0.18115
1.1 | 0.19433 | 0.17368 | 0.24153 | 0.22709
1.15 | 0.2282 | 0.21089 | 0.28913 | 0.27663
1.2 | 0.2646 | 0.25074 | 0.33902 | 0.32864
1.25 | 0.30308 | 0.29259 | 0.3902 | 0.38198
1.3 | 0.34312 | 0.3358 | 0.4417 | 0.43553
1.35 | 0.38417 | 0.37972 | 0.49259 | 0.4883
1.4 | 0.42567 | 0.42372 | 0.54207 | 0.53942
1.45 | 0.46708 | 0.46725 | 0.58949 | 0.58821
1.5 | 0.50792 | 0.50983 | 0.63431 | 0.63414
1.55 | 0.54774 | 0.55102 | 0.67617 | 0.67687
1.6 | 0.58618 | 0.5905 | 0.71483 | 0.71617
1.65 | 0.62294 | 0.628 | 0.75018 | 0.75197
1.7 | 0.65779 | 0.66334 | 0.7822 | 0.78428
1.75 | 0.69058 | 0.6964 | 0.81098 | 0.81321
1.8 | 0.7212 | 0.72713 | 0.83664 | 0.83892
1.85 | 0.74962 | 0.7555 | 0.85936 | 0.86161
1.9 | 0.77583 | 0.78156 | 0.87936 | 0.88152
1.95 | 0.79986 | 0.80537 | 0.89685 | 0.89889
2 | 0.8218 | 0.82702 | 0.91208 | 0.91397

## State_Definitions
Failure states and dependency
State costs are same-failure-unit DRs; localized costs are explicit T4 screening assumptions
Family | State | Cost ratio | Description | Tier | Dependency rule
module | MODULE_DS0_NO_DIRECT_DAMAGE | 0 | No direct module-field repair | T4 | Preserve unless structure terminal
module | MODULE_DS1_LOCALIZED_REPLACEMENT | 0.1 | Localized modules/frames/clamps | T4 | May coexist with nonterminal structure; dependence uncalibrated
module | MODULE_DS2_FIELD_REPLACEMENT | 1 | Replace exposed module field | T4 | Forced when structure is terminal
structure | STRUCT_DS0_NO_DIRECT_DAMAGE | 0 | No structural repair | T4 | No module cascade
structure | STRUCT_DS1_LOCALIZED_REPAIR | 0.15 | Localized joints/rails/braces/drive-row work | T4 | No automatic full module replacement
structure | STRUCT_DS2_REPLACE_STRUCTURE_MODULES_SALVAGEABLE | 1 | Replace exposed structure; module hardware assumed salvageable/reinstallable | T4 | No central module non-salvage cascade
structure | STRUCT_DS3_DESTRUCTIVE_COLLAPSE_MODULES_NONSALVAGEABLE | 1 | Destructive collapse; colocated module hardware assumed nonsalvageable | T4 | Central T4 rule; also show full/no-salvage bounds
Loss assembly: central T4 uses DS3 destructive-collapse non-salvage; retain full-salvage and no-salvage-on-any-replacement bounds. Replacement support remains outside intrinsic DR.

## KATs
Known-answer and rejection tests
Expected values are governed fixtures; the Python validator independently evaluates every test
Test ID | Architecture | Failure unit | Axis | Expected central DR | Status | Curve | Source | Notes
fixed_direct_x1_module | fixed_tilt_ground_mount_screening_v1 | PV_FIXED_TILT_MODULE_FIELD | 1 | 0.13543 | conditional | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | direct equation fixture from the governed proposed artifact | Tests fixed-tilt direct-pressure routing, the central equation, all scenario bounds, and probability closure.
fixed_direct_x1_structure | fixed_tilt_ground_mount_screening_v1 | PV_FIXED_TILT_SUPPORT_STRUCTURE | 1 | 0.10932 | conditional | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | direct equation fixture from the governed proposed artifact | Tests the separate fixed-tilt structural value atom; it must not inherit module DR.
fixed_speed_proxy_30_over_40 | fixed_tilt_ground_mount_screening_v1 | PV_FIXED_TILT_MODULE_FIELD | 0.5625 | 0.0087664 | conditional | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | screening proxy equation in the governed proposed artifact | Tests the only permitted fixed-tilt speed proxy and preserves the 10 m source lineage.
tracker_qualified_eta_0_75 | single_axis_tracker_qualified_screening_v1 | PV_TRACKER_MODULE_FIELD | 0.75 | 0.029954 | conditional | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | qualified tracker-axis equation; 0.75 operational flag anchored by FM DS 7-106 | The 0.75 flag is not a damage threshold and does not choose a favorable curve.
tracker_qualified_eta_1_structure | single_axis_tracker_qualified_screening_v1 | PV_TRACKER_SBOS_ASSEMBLY | 1 | 0.13983 | conditional | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | direct equation fixture from the governed proposed artifact | A 2P tracker is supported only through its exact named aeroelastic Ucrit; 2P receives no generic modifier.
foundation_is_withheld | fixed_tilt_ground_mount_screening_v1 | PV_FOUNDATION | withheld | null | withheld | null | failure-unit coverage and capability declaration | Withheld is null, never zero and never inherited from structure.
Rejection test | Expected code | Source | Notes
reject_missing_pathway | PATHWAY_ID_REQUIRED | pathway contract | Pathway has no default.
reject_hurricane_pathway | PATHWAY_ID_UNKNOWN | neighboring-wind boundary | Hurricane/TC wind cannot inherit the convective curve.
reject_missing_architecture | ARRAY_ARCHITECTURE_REQUIRED | asset architecture contract | Fixed tilt and tracker cannot share an implicit default.
reject_rooftop | ARRAY_ARCHITECTURE_UNSUPPORTED | asset scope | Rooftop building interaction requires a different curve.
reject_unbridged_10m_fixed | PRESSURE_INDEX_REQUIRED | convective height/profile boundary | A 10 m gust is never the fixed-tilt axis.
reject_fixed_proxy_without_profile_bridge | CONVECTIVE_PROFILE_BRIDGE_REQUIRED | convective height/profile boundary | The speed proxy requires a named non-synoptic bridge.
reject_fixed_direct_without_demand_bridge | AERODYNAMIC_DEMAND_BRIDGE_REQUIRED | fixed-tilt demand bridge contract | Even a delivered pressure index must identify its qualified bridge.
reject_tracker_without_ucrit | AERODYNAMIC_DEMAND_BRIDGE_REQUIRED | tracker axis contract | There is no universal tracker critical speed.
reject_tracker_without_1p_2p_identity | ARRAY_ARCHITECTURE_UNSUPPORTED | tracker selector contract | 1P/2P identity is mandatory even though Ucrit carries its numeric effect.
reject_fixed_unit_on_tracker | FAILURE_UNIT_NOT_APPLICABLE_TO_ARCHITECTURE | selector routing contract | Cross-architecture numerical fallback is prohibited.
reject_axis_above_two | AXIS_OUTSIDE_VALID_RANGE | bounded extrapolation policy | The screening model is withheld outside its declared range.
reject_bad_array_zone | CONDITIONER_VALUE_UNSUPPORTED | conditioner contract | The whole site cannot silently stand in for an array zone.
reject_tracker_stow_state_on_fixed_tilt | CONDITIONER_VALUE_UNSUPPORTED | selector/conditioner routing contract | Fixed tilt must materialize tracker-only state as not_applicable, never as a stow condition.
reject_tracker_qualification_angle_mismatch | TRACKER_QUALIFICATION_BASIS_MISMATCH | exact-system tracker qualification contract | The event attained angle must match the Ucrit qualification basis before DR or the FM action flag is emitted.
reject_negative_transient_rise_time | CONDITIONER_VALUE_UNSUPPORTED | typed conditioner contract | A duration descriptor must be nonnegative or explicitly unknown.
reject_command_only_tracker_position | TRACKER_QUALIFICATION_BASIS_MISMATCH | attained-state qualification contract | A command log does not prove the physical tracker position and cannot earn a favorable Ucrit basis.
Pin test | Expected | Notes
pin_exact_computed_sha | pass | The validator substitutes the exact current artifact byte SHA.
pin_missing_docs | ARTIFACT_PIN_INCOMPLETE | Partial pins reject.
pin_wrong_sha | ARTIFACT_PIN_MISMATCH | A different byte artifact rejects.
pin_wrong_model | ARTIFACT_PIN_MISMATCH | Model/docs/schema/SHA identity is atomic.
Loss rejection test | Expected code | Notes
loss_reject_missing_currency | EXPLICIT_VALUE_AND_EXPOSURE_REQUIRED | Currency is part of the atomic value basis.
loss_reject_per_kw_without_capacity | EXPLICIT_VALUE_AND_EXPOSURE_REQUIRED | Per-kWdc values cannot become currency loss without capacity.
loss_reject_missing_parent_event | EXPLICIT_VALUE_AND_EXPOSURE_REQUIRED | Parent convective identity is required for event-family deduplication.
loss_reject_noncolocated_common_fraction | EXPLICIT_VALUE_AND_EXPOSURE_REQUIRED | Different module/structure footprints require separate exposure objects outside the common-zone helper.

## Value_Crosswalk
Value crosswalk
Primary Q1-2025 rows plus tracker/fixed sensitivities; no implicit default profile
value_source_id | source_location | row_or_bucket_id | row_or_bucket_label | value | unit | financial_class | failure_unit_id | role_in_loss | include_in_direct_denominator | allocation_rule | double_count_guardrail | status | notes
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!2 | SOLAR_VALUE_002_MODULE | Module hardware + manufacturing allocation | 291.21485143992487 | 2024_USD_per_kWdc | direct_hardware | PV_FIXED_TILT_MODULE_FIELD¦PV_TRACKER_MODULE_FIELD | direct_vulnerable_value | true | Use only for the active selected architecture and explicit site exposure; site/BOM value overrides. | Never charge both fixed and tracker records or charge module replacement again after the terminal-structure cascade. | mapped_reference_only | The benchmark is a reference value, not an implicit site default or curve cap.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!3 | SOLAR_VALUE_003_MOUNTING | Tracker/racking hardware | 109.98972602739727 | 2024_USD_per_kWdc | direct_hardware | PV_FIXED_TILT_SUPPORT_STRUCTURE¦PV_TRACKER_SBOS_ASSEMBLY | direct_vulnerable_value | true | Use only for the active selected architecture when the site BOM supports transfer; fixed tilt otherwise requires an explicit site value. | Do not split torque tube, drive, rails, piles and foundations beyond source support or sum tracker and racking curves. | mapped_reference_only | Architecture-generic repository row; tracker/fixed composition transfer remains limited.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!4 | SOLAR_VALUE_004_FOUNDATION | Driven piers + inverter pad | 31.12448715327472 | 2024_USD_per_kWdc | direct_hardware | PV_FOUNDATION | withheld | false | Retain for reconciliation; require architecture/geotechnical split and separate fragility before loss. | Never inherit active support-structure DR or exposure. | withheld | Mixed foundation bucket.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!5 | SOLAR_VALUE_005_INVERTER | Central inverter hardware | 32.306366410372384 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_ELECTRICAL | withheld | false | Separate point-asset exposure and direct mechanism required. | Do not apply array pressure DR or array exposed fraction. | withheld | Direct wind pressure is not a supported inverter fragility.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!6 | SOLAR_VALUE_006_COMBINER | Combiner boxes | 6.82625 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_ELECTRICAL | withheld | false | Split enclosure, location, debris and ingress pathways before modeling. | Do not pool with inverter, cable or module response. | withheld | No direct aerodynamic curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!7 | SOLAR_VALUE_007_CABLE | AC and DC conductors and project electrical line | 69.3201119402985 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_ELECTRICAL | withheld | false | Split exposed, buried, conduit, termination and line segments. | Do not reuse array zone exposure. | withheld | Mixed line-asset value.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!8 | SOLAR_VALUE_008_MV | Transformer, switches, breakers and substation | 106.50466417910448 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_ELECTRICAL | withheld | false | Split point assets and mechanisms. | Do not apply module or structure DR. | withheld | No direct convective fragility.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!9 | SOLAR_VALUE_009_GROUNDING | Grounding and lightning protection | 8.385 | 2024_USD_per_kWdc | direct_hardware | PV_POWER_CONVERSION_AND_ELECTRICAL | withheld | false | Retain for reconciliation; lightning is a separate pathway. | No wind-pressure inheritance. | withheld | Mixed grounding/lightning row.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!10 | SOLAR_VALUE_010_SCADA | System monitor | 1.31 | 2024_USD_per_kWdc | direct_hardware | PV_SCADA_COMMUNICATIONS | withheld | false | Location and exposure split required. | Tracker control state may condition demand but is not a duplicate SCADA loss by default. | withheld | No direct aerodynamic curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!11 | SOLAR_VALUE_011_NETWORK | Grid network upgrade | 0.0 | 2024_USD_per_kWdc | excluded_nonphysical | OUTSIDE_PHYSICAL_CELL | excluded | false | Exclude. | Never reintroduce through physical loss. | excluded | Zero reference row.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!12 | SOLAR_VALUE_012_SBOS_LABOR | Mounting field labor | 43.273972602739725 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | support_once | false | Allocate once after direct module/structure state and terminal cascade using a qualified reinstatement rule. | No intrinsic DR and no duplication inside both failure-unit denominators. | mapped_support_rule_open | Not all greenfield labor necessarily recurs.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!13 | SOLAR_VALUE_013_EBOS_LABOR | Electrical field labor | 39.447761194029844 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | support_once | false | Allocate only when separately supported electrical work occurs. | Do not scale by array DR by default. | mapped_support_rule_open | No independent curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!14 | SOLAR_VALUE_014_CIVIL | Grading, fencing, roads and buildings | 31.223744292237445 | 2024_USD_per_kWdc | mixed_civil_replacement_bucket | PV_CIVIL_INFRA | withheld | false | Split line, area and point assets before exposure/damage. | Do not reuse array zone exposure or structure DR. | withheld | Mixed civil bucket.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!15 | SOLAR_VALUE_015_GENERAL_SUPPORT | Site management, equipment rental and inspection | 106.86876712328767 | 2024_USD_per_kWdc | replacement_support_cost | PV_REPLACEMENT_SUPPORT | support_once | false | Allocate once at claim/repair scope; site rule required. | Do not multiply independently by module and structure DR. | mapped_support_rule_open | No independent curve.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map!16-17 | SOLAR_VALUE_016_017_EXCLUDED | Officework and other soft/nonphysical value | 242.20429763733296 | 2024_USD_per_kWdc | excluded_soft_sunk_nonphysical | OUTSIDE_PHYSICAL_CELL | excluded | false | Exclude from physical denominator unless an explicit insured-value contract says otherwise. | Never turn installed-TIV share into an intrinsic DR cap. | excluded | Installed 1120 minus physical 877.7957023626668.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_DIRECT | Direct hardware subtotal | 656.9814571503722 | 2024_USD_per_kWdc | reconciliation | ALL_DIRECT_FAILURE_UNITS | reference_only | false | Reconcile rows 2–10; never pool under one curve. | Array-only output covers module and mounting rows, not this subtotal. | reconciled | Reference only.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_PHYSICAL | Physical replaceable reference basis | 877.7957023626668 | 2024_USD_per_kWdc | reconciliation | ALL_PHYSICAL_FAILURE_UNITS_AND_SUPPORT | reference_only | false | Physical reference equals direct hardware plus replacement/civil/support rows. | Withheld rows are unknown, not zero; do not report array DR as full-physical DR. | reconciled | Installed equals physical plus 242.20429763733296.
NLR_Q1_2025_UPV_PV_ONLY_2024_USD | docs/method/value_basis/solar_wind_value_breakdown.xlsx::Solar_Map summary | SOLAR_VALUE_SUMMARY_INSTALLED | Installed CAPEX reference basis | 1120.0 | 2024_USD_per_kWdc | installed_reference | OUTSIDE_INTRINSIC_CURVE | reference_only | false | Reporting conversion only with explicit numerator label. | Not an intrinsic curve denominator or cap. | reconciled | Array module+mounting reference is 0.35821837273868046 of installed.
NREL_Q1_2024_MMP_TRACKER_2023_USD | DOE PV cost benchmark Figure 1 | TRACKER_SENS_MODULE | One-axis-tracker module MMP | 336.0 | 2023_USD_per_kWdc | sensitivity_direct_hardware | PV_TRACKER_MODULE_FIELD | sensitivity_only | false | Use only as a source-native tracker sensitivity with the same vintage profile. | Never blend with 2024 USD primary rows. | sensitivity_only | Tracker benchmark.
NREL_Q1_2024_MMP_TRACKER_2023_USD | DOE PV cost benchmark Figure 1 | TRACKER_SENS_SBOS | One-axis-tracker structural BOS MMP | 140.0 | 2023_USD_per_kWdc | sensitivity_direct_hardware | PV_TRACKER_SBOS_ASSEMBLY | boundary_mismatched_sensitivity_only | false | The source combines tracker/racking/pile/foundation content; do not use 140 as the above-ground SBOS curve denominator unless foundation content is reconciled by a governed BOM. | Do not split torque tube, drive, racking, piles and foundation beyond source support or compare its loss directly to the foundation-excluding primary record. | sensitivity_boundary_mismatch | Tracker benchmark; useful only for whole-SBOS sensitivity until the boundary is reconciled.
NREL_Q1_2024_MMP_TRACKER_2023_USD | DOE PV cost benchmark Figure 1 | TRACKER_SENS_INSTALLED | One-axis-tracker installed MMP | 1119.0 | 2023_USD_per_kWdc | installed_reference | OUTSIDE_INTRINSIC_CURVE | sensitivity_only | false | Reconcile 336+33+140+186+229+62+133. | Not a DR denominator. | sensitivity_only | Fieldwork 229 must remain separate from direct hardware.
NREL_Q1_2021_COST_BENCHMARK | NREL Q1-2021 benchmark PDF p. 27 | FIXED_TILT_STRUCTURE_RANGE | Structural components, fixed tilt or one-axis tracker | 90.0-120.0 | 2020_USD_per_kWdc | screening_value_range | PV_FIXED_TILT_SUPPORT_STRUCTURE | reference_range_only | false | Require explicit site value; use range only for sensitivity. | Do not assign a point value or assume the endpoints separately identify fixed tilt and tracker. | withheld_as_default | Older and architecture-combined range.

## Sources
Source register
Every source has an exact endpoint, permitted inference and prohibited transfer
source_id | full_citation | source_class | accessed_on | primary_url | exact_locator | native_axis_or_endpoint | direct_support | prohibited_support | evidence_role | tier | status
PV_TRACKER_DOWNBURST_2025 | Álvarez et al. Downburst-Induced Loads on a Six-Row Array of Ground-Mounted Solar Trackers. Proceedings of the 10th International Conference on Advances in Experimental Structural Engineering, 2025. | peer-reviewed conference experiment | 2026-07-12 | https://doi.org/10.1007/978-3-031-98893-6_6 | pp. 54–63; §§2–6; especially pp. 57–62 | 1:20 six-row rigid tracker model; 576 pressure taps; eight vertical-jet downburst repeats; pressure-time histories | Transient ramp/plateau/decay, primary-vortex surge, row and tilt dependence, downburst knowledge gap | Critical speed, component capacity, failure probability, damage state, economic DR, full-scale threshold | hazard mechanism / axis / conditioner | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
IEA_PVPS_EXTREME_WEATHER_2025 | IEA PVPS Task 13. Operational and Economic Impacts of Extreme Weather on PV Power Plants. T13-33:2025. | international laboratory synthesis | 2026-07-12 | https://iea-pvps.org/wp-content/uploads/2025/12/IEA-PVPS-T13-33-2025-REPORT-Extreme-Weather-Impacts.pdf | §3.2.2 pp. 24–25; §§3.4–3.6 pp. 25–28 | reported straight-line wind cases around 22–28 m/s; Oakey and Lamar tracker narratives | Observed below-design damage is possible; 1P/2P, stow, perimeter and anemometer state are load-bearing | Population fragility, normalized DR, exact value denominator, literal threshold or fitted median; Lamar citation is uncertain | field anchor / asset taxonomy | T3_engineering_proxy_or_adjacent_empirical | RETAINED_AS_SCREENING_CONSTRAINT
VALENTIN_TRACKER_FAILURE_2022 | Valentín et al. Failure Investigation of a Solar Tracker Due to Wind-Induced Torsional Galloping. Engineering Failure Analysis 135, 106137 (2022). | peer-reviewed forensic case | 2026-07-12 | https://doi.org/10.1016/j.engfailanal.2022.106137 | §§3.2–3.3, 4.3 and 6 | one exposed flat tracker failed; nearby station about 16.7 m/s; rotation, module, shaft and pillar damage | Tracker cascade sequence and importance of angle/exposure | Convective attribution, local threshold, population probability, economic DR | mechanism / vulnerable-architecture bound | T3_engineering_proxy_or_adjacent_empirical | RETAINED_WITH_TRANSFER_LIMIT
CPP_TRACKER_INSTABILITY_2015 | Rohr, Bourke and Banks. Torsional Instability of Single-Axis Solar Tracking Systems. 2015. | engineering wind-tunnel / CFD paper | 2026-07-12 | https://www.cppwind.com/wp-content/uploads/2020/12/Torsional-Instability-of-Single-Axis-Solar-Tracking-Systems-Rohr-Bourke-Banks-2015.pdf | pp. 1–7; especially pp. 5–7 | sectional critical velocity and tracker twist under ABL flow | System-specific critical-speed and angle-conditioned tracker axis | Universal 40 m/s threshold, downburst response, DR or loss | tracker axis / mechanism | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
TRACKER_LAYOUT_AEROELASTIC_2025 | Frontini et al. Key Parameters Influencing Wind-Induced Aeroelastic Responses of Single-Axis Solar Trackers in Photovoltaic Plants. Solar Energy 2025, 113232. | peer-reviewed wind-tunnel and FEM study | 2026-07-12 | https://doi.org/10.1016/j.solener.2024.113232 | abstract; stability map Fig. 7; stress envelopes Fig. 12 | critical response by tracker position, pitch, direction and ground-coverage ratio | Required row, pitch, direction and layout fields | Transfer of tested critical speeds to another tracker or to downburst loading | tracker selectors / conditioners | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
PV_TRACKER_AEROELASTIC_2024 | Rodríguez-Casado et al. Experimental Benchmark for the 3D Wind Tunnel Testing of Torsional Aeroelastic Instabilities in Single-Axis Solar Trackers. JWEIA 2024, 105838. | peer-reviewed aeroelastic benchmark | 2026-07-12 | https://doi.org/10.1016/j.jweia.2024.105838 | abstract and §§1–3 | 3D aeroelastic critical velocity by design and tilt in two tunnels | Exact-system named Ucrit normalization and qualification identity | Generic production-tracker fragility or damage probability | tracker axis / qualification | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
TRACKER_FIELD_MODAL_2024 | Koekemoer et al. Field Measurements of Wind Load Effects in a Photovoltaic Single-Axis Tracker Mounting Rail. JWEIA 2024, 105876. | peer-reviewed full-scale field measurements | 2026-07-12 | https://doi.org/10.1016/j.jweia.2024.105876 | abstract; 109-day campaign | 1P tracker torsional and bending modal response by direction and pile position | 1P/2P and modal/layout differentiation | No-damage threshold or destructive convective response | tracker mechanism / future calibration | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
FIXED_TILT_WIND_DESIGN_2020 | Browne et al. A Wind Load Design Method for Ground-Mounted Multi-Row Solar Arrays Based on a Compilation of Wind Tunnel Experiments. JWEIA 2020, 104294. | peer-reviewed ABL wind-tunnel synthesis | 2026-07-12 | https://doi.org/10.1016/j.jweia.2020.104294 | abstract and §§1–5 | fixed-tilt static/dynamic pressure coefficients and perimeter/field zones | Separate fixed-tilt load bridge and array zoning | Downburst coefficients, tracker aeroelasticity, failure probability or DR | fixed-tilt axis / zone design | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
SOLAR_JOINT_CYCLIC_2025 | Du et al. Cyclic Demands on Solar Structural Joints under Wind Loading. Journal of Structural Engineering, 2025. | peer-reviewed CFD/FEA/hazard study | 2026-07-12 | https://doi.org/10.1061/JSENDH.STENG-14435 | abstract and conclusions | lifetime clamp/joint cyclic demand | Joint coverage and acute-versus-fatigue boundary | Single-occurrence convective DR or lifetime-to-peak conversion | failure-unit design / boundary | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
SOLAR_CRITICAL_JOINTS_2025 | Robinson. Maturing Rational Design Methodologies and Industry Consensus Engineering Standards: Critical Fastened Joints – Solar PV Industry. LBNL, 2025. | public-laboratory engineering report | 2026-07-12 | https://doi.org/10.20357/B7VG76 | abstract and report | joint failure, racking deflection/twist and load feedback | Attachment/joint condition and cascade logic | Wind-to-failure population or cost fraction | failure mechanism / condition | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
DOE_PV_OWNER_GUIDE_2021 | U.S. DOE/FEMP and GSA. PV System Owner’s Guide to Identifying, Assessing, and Addressing Weather Vulnerabilities, Risks, and Impacts. 2021. | official field-audit guidance | 2026-07-12 | https://www.energy.gov/sites/default/files/2021-09/pv-system-owners-guide-to-weather-vulnerabilities.pdf | §5; PDF pp. 43–50 for clamps/racking; derecho context pp. 56–58 | field-audit vulnerabilities and observed module, clamp, fastener, racking, wiring and enclosure mechanisms | Failure-unit coverage, dependency, audit and conditioner fields | Numerical utility-scale convective fragility, parameter median, dispersion or loss cap | mechanism / failure-unit / conditioner | T2_public_lab_standard_or_physics | RETAINED_QUALITATIVE
NREL_WEATHER_IMPACTS_2021 | Walker et al. Weather Impacts on Solar PV Operations: Summary of the 2021 PV Reliability Workshop. LBNL/NREL/Sandia, 2021. | public-laboratory workshop synthesis | 2026-07-12 | https://escholarship.org/content/qt5t8569hf/qt5t8569hf_noSplash_f0e76891c1cd44233507d7c5afbad87a.pdf | pp. 23–25, 30–32, 39–42 and 56–58 | field cases, clamp/fastener failure, module/rack dynamics, thunderstorm/downburst context | Mechanism, dependency, below-design failure possibility and open evidence seams | Curve calibration, universal threshold or repair-cost ratio | mechanism / evidence-gap synthesis | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
FM_DS_7_106_2026 | FM. Data Sheet 7-106: Ground-Mounted Solar Photovoltaic Power. April 2026. | insurer engineering standard | 2026-07-12 | https://www.fm.com/-/media/project/publicwebsites/fmglobal/documentum-new/data-sheet-individual/07-hazards/fmds07106.pdf | §§2.1.2.3–2.1.2.4 pp. 3–4; §3.1 pp. 10–11 | static/dynamic/aeroelastic review; multiple anemometers; stow trigger 25% below tested instability speed | Ucrit qualification, monitoring and 0.75 action flag | 0.75 as damage threshold, hard zero or fragility ordinate | tracker operational gate | T2_public_lab_standard_or_physics | RETAINED_AS_GATE_NOT_CURVE
ASTM_E1830_2025 | ASTM E1830-15(2025). Standard Test Methods for Determining Mechanical Integrity of Photovoltaic Modules. | consensus test standard | 2026-07-12 | https://store.astm.org/e1830-15r25.html | scope §§1.1–1.4; significance §4 | 2400 Pa static, 1440 Pa cyclic, twist test; no pass/fail level | Module qualification metadata and physical/electrical endpoints | Universal wind speed, failure probability or economic DR | module test / selector | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
IEC_62782_2016 | IEC TS 62782:2016. Photovoltaic modules — Cyclic (dynamic) mechanical load testing. | international test standard | 2026-07-12 | https://webstore.iec.ch/en/publication/24310 | scope | alternating uniform module load test | Module-test provenance and fatigue susceptibility | Transient downburst, plant fragility or DR | module test / selector | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
IEC_62817 | IEC 62817:2014+A1:2017. Photovoltaic systems — Design qualification of solar trackers. | international qualification standard | 2026-07-12 | https://webstore.iec.ch/en/publication/61127 | scope and qualification sequence | tracker design qualification | Exact tracker architecture/qualification identity and testing context | Site-specific structure/foundation certification, Ucrit for an unnamed tracker, or fragility | tracker selector / qualification | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
ASCE_7_22 | ASCE/SEI 7-22. Minimum Design Loads and Associated Criteria for Buildings and Other Structures. | consensus design standard | 2026-07-12 | https://www.asce.org/publications-and-news/codes-and-standards/asce-sei-7-22 | Ch. 29 §29.4.5; Ch. 31 §31.4.5; Ch. 26 symbols | fixed-tilt ground-mount wind design; 3-second gust at 10 m Exposure C source definition | Design normalization and fixed-tilt scope | Failure capacity, D50, tracker aeroelastic response or downburst profile | design anchor / axis lineage | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
ASCE_49_21 | ASCE/SEI 49-21. Wind Tunnel Testing for Buildings and Other Structures. | consensus wind-tunnel standard | 2026-07-12 | https://www.asce.org/communities/institutes-and-technical-groups/structural-engineering-institute/committees/sei-board-of-governors/sei-technical-community-executive-committee/asce-49---wind-tunnel-testing | §2.3.2 nonsynoptic winds | wind-tunnel requirements including downbursts and other nonsynoptic winds | Named downburst/non-synoptic and tracker qualification bridge | PV fragility or damage parameters | test-method anchor | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
NIST_THUNDERSTORM_PROFILES_2011 | Lombardo et al. Thunderstorm Characteristics of Importance to Wind Engineering Part II: Profiles, Gust Factors and Other Observations. JWEIA 2011. | peer-reviewed primary field analysis | 2026-07-12 | https://www.nist.gov/publications/thunderstorm-characteristics-importance-wind-engineering-part-ii-profiles-gust-factors | abstract and paper; ramp-up/profile/gust-factor sections | nonstationary ramp-up, vertical components, profile and gust-factor variability | Reject silent stationary-ABL equivalence and ordinary default profile conversion | Solar failure threshold or DR | hazard-axis boundary | T2_public_lab_standard_or_physics | RETAINED
FULL_SCALE_DOWNBURST_2018 | Gunter and Schroeder. Investigation of a Downburst Loading Event on a Full-Scale Low-Rise Building. JWEIA 2018. | peer-reviewed full-scale event study | 2026-07-12 | https://doi.org/10.1016/j.jweia.2018.09.020 | highlights and results | about 30 s ramp; peak near 4 m; direction change up to about 30° over 50 m | Rise time, direction change and non-power-law bridge requirement | PV fragility or structural transfer coefficients | hazard-axis boundary | T2_public_lab_standard_or_physics | RETAINED_WITH_ASSET_TRANSFER_LIMIT
DERECHO_MULTISCALE_2025 | Wagner et al. Detecting and Interpreting Wind Damage at Multiple Scales in the 10 August 2020 Derecho Using UAS, Satellite, and Radar. Weather and Forecasting, 2025. | peer-reviewed event reconstruction | 2026-07-12 | https://doi.org/10.1175/WAF-D-24-0198.1 | abstract; pp. 1–2 and 12–14 | MCS flow, downburst clusters, mesovortices, tornadoes and roughly 10 m damage variability | Derecho label requires local mechanism partition and parent event identity | One derecho-wide demand or PV parameter | event partition / boundary | T2_public_lab_standard_or_physics | RETAINED
NWS_DOWNBURST_TAXONOMY | U.S. National Weather Service. Downbursts; NWS Glossary; NSSL Thunderstorm FAQ. | official meteorological definitions | 2026-07-12 | https://www.weather.gov/spotterguide/downbursts | definitions | downburst, microburst, macroburst, gust front and derecho taxonomy | Pathway scope vocabulary | 58 mph warning threshold as PV damage onset | hazard scope | T2_public_lab_standard_or_physics | RETAINED
DOE_FEMP_STORM_HARDENING_2020 | Elsworth and Van Geet. Solar Photovoltaics in Severe Weather: Cost Considerations for Storm Hardening PV Systems for Resilience. NREL/TP-7A40-75804, 2020. | public-laboratory cost report | 2026-07-12 | https://docs.nrel.gov/docs/fy20osti/75804.pdf | Table 1 pp. 2–3; scope pp. 3–4 | incremental preventive costs for fasteners, through-bolts, modules, rails, piers and racking | Selector economics and plausibility only | Repair cost, damage-state ratio, tracker value or fragility | hardening context / rejected cost transfer | T2_public_lab_standard_or_physics | RETAINED_WITH_TRANSFER_LIMIT
NREL_Q1_2021_COST_BENCHMARK | Ramasamy et al. U.S. Solar Photovoltaic System and Energy Storage Cost Benchmarks: Q1 2021. NREL/TP-7A40-80694. | public-laboratory cost benchmark | 2026-07-12 | https://www.govinfo.gov/content/pkg/GOVPUB-E9-PURL-gpo184395/pdf/GOVPUB-E9-PURL-gpo184395.pdf | PDF p. 27 utility-scale modeling inputs | structural components 0.09–0.12 2020 USD/Wdc for fixed tilt or one-axis tracking | Fixed-tilt screening value bracket | Architecture-specific point value, fragility or current-dollar replacement cost | fixed-tilt value sensitivity | T2_public_lab_standard_or_physics | RETAINED_AS_RANGE_ONLY
NREL_Q1_2024_MMP_TRACKER | DOE/NREL PV System Cost Model Q1 2024 market price benchmark for a 100 MWdc one-axis-tracker plant. | public-laboratory cost benchmark | 2026-07-12 | https://www.energy.gov/cmei/systems/solar-photovoltaic-system-cost-benchmarks | Figure 1 source-native MMP rows | 336 module, 140 SBOS, 33 inverter, 186 EBOS, 229 fieldwork, 1119 total; 2023 USD/kWdc | Tracker architecture sensitivity and row-level reconciliation | Fixed-tilt point value, component fragility or blended primary reference | tracker value sensitivity | T2_public_lab_standard_or_physics | RETAINED_FOR_VALUE_ONLY
NREL_NLR_Q1_2025_PV_BENCHMARK | Basore et al. Q1-2025 Solar Photovoltaic System Cost Benchmarks. NLR/OT-7A40-97930; data catalog submission 304. | official cost dataset | 2026-07-12 | https://doi.org/10.7799/3009689 | dataset and governed Solar_Map crosswalk | 2024 USD/kWdc utility-PV installed and value rows | Repository-current reference-value reconciliation | Site appraisal, architecture-specific BOM, vulnerability or exposed fraction | primary reference value | T2_public_lab_standard_or_physics | RETAINED_FOR_VALUE_ONLY
VALUE_SOLAR_WORKBOOK | damage_modeling/docs/method/value_basis/solar_wind_value_breakdown.xlsx. | internal governed derivation | 2026-07-12 | https://data.nlr.gov/submissions/304 | Solar_Map rows 2–17 | 2024 USD/kWdc row-level direct, support and excluded values | Reference denominator and row mapping | Implicit site value, at-risk fraction or fragility | value crosswalk | T2_public_lab_standard_or_physics | RETAINED_FOR_REFERENCE_ONLY
NO_DIRECT_CALIBRATION_SOURCE | Governed provenance marker: the bounded review found no retained matched dataset joining site-local convective demand, architecture/state, inspected disposition, and same-unit repair cost for utility PV. | negative-evidence control marker | 2026-07-12 |  | BOUNDED_EVIDENCE_SEARCH_LOG_strong_wind_solar__model_v2_0__docs_r1.md | not applicable | Explains why numerical medians, beta, zero boundary and local state costs are T4 assumptions | Evidence that no such data exists outside the recorded search; any numerical support | parameter-withholding / T4 marker | T4_placeholder_or_expert_judgment | CONTROL_MARKER_NOT_EVIDENCE
LEGACY_SWS_V1 | Current canonical strong_wind_solar model v1.0/docs r3 artifact and workbook. | legacy implementation audit | 2026-07-12 |  | docs/cells/strong_wind_solar/current/ | gust mph, effective demand ratio, five logistics and value shares | Exact legacy reproduction and migration comparison | Scientific calibration for v2 | legacy audit only | T4_placeholder_or_expert_judgment | REJECTED_FOR_CALIBRATION

## Claim_Register
Claim / parameter provenance
No orphan load-bearing claims; each row states what may and may not be inferred
claim_id | claim_text | claim_type | source_ids | exact_locator | evidence_tier | parameter_or_rule | adoption_status | permitted_inference | prohibited_inference | reasoning | update_trigger
SWS2-C001 | Convective wind belongs in the existing strong_wind_solar cell rather than a parallel overlapping cell. | governance_decision | LEGACY_SWS_V1;NWS_DOWNBURST_TAXONOMY | current cell scope and scope guide | T4_placeholder_or_expert_judgment | cell_id=strong_wind_solar | adopt | Create a proposed major revamp while current v1 remains canonical. | Create an overlapping convective_wind_solar artifact. | The current cell already claims straight-line/derecho wind, so a pathway-aware major revision preserves identity. | Approved repository taxonomy change.
SWS2-C002 | pathway_id is exactly straight_line_convective and has no default or speed-based inference. | governance_decision | NWS_DOWNBURST_TAXONOMY;DERECHO_MULTISCALE_2025 | scope taxonomy and event reconstruction | T2_public_lab_standard_or_physics | pathway routing | adopt | Route local non-tornadic thunderstorm outflow to this proposal. | Infer convective, tornado or hurricane pathway from intensity alone. | Causal wind-field identity is load-bearing. | A later schema replaces explicit pathway routing.
SWS2-C003 | The pathway includes downburst, microburst, macroburst, gust front, non-tornadic outflow and locally resolved derecho outflow. | source_interpretation | NWS_DOWNBURST_TAXONOMY;DERECHO_MULTISCALE_2025 | definitions; derecho pp. 1–2 and 12–14 | T2_public_lab_standard_or_physics | hazard_scope.included | adopt | Use site-local convective demand with parent event identity. | Use one derecho-wide demand at every array zone. | Derechos contain multiple local mechanisms and damage scales. | Meteorological taxonomy or event-partition evidence changes.
SWS2-C004 | Tropical cyclone, tornado, synoptic/downslope wind, hail, debris impact, rain ingress and lifetime fatigue are excluded. | governance_decision | DERECHO_MULTISCALE_2025;SOLAR_JOINT_CYCLIC_2025;IEA_PVPS_EXTREME_WEATHER_2025 | boundary memo and source endpoints | T3_engineering_proxy_or_adjacent_empirical | neighboring hazard boundary | adopt | Share solar anatomy/value only through explicit separate review. | Reuse numerical parameters across wind mechanisms or mix impact/ingress loss into pressure DR. | Duration, profile, debris, exposure and endpoint differ. | A documented equivalence study passes.
SWS2-C005 | Downburst loading is transient, row dependent and not equivalent to stationary ABL loading. | source_finding | PV_TRACKER_DOWNBURST_2025;NIST_THUNDERSTORM_PROFILES_2011;FULL_SCALE_DOWNBURST_2018 | Álvarez pp. 57–62; NIST profile/ramp sections; Gunter results | T2_public_lab_standard_or_physics | axis and bridge rule | adopt | Require a named non-synoptic profile/demand bridge and transient descriptors. | Apply an ordinary default power-law or stationary coefficient without qualification. | Field and wind-tunnel evidence show ramp, direction/profile and vortex differences. | Validated universal convective conversion becomes available.
SWS2-C006 | Fixed-tilt and tracker arrays require separate numerical records. | source_finding | FIXED_TILT_WIND_DESIGN_2020;PV_TRACKER_AEROELASTIC_2024;IEA_PVPS_EXTREME_WEATHER_2025 | Browne §§1–5; tracker benchmark §§1–3; IEA §§3.4–3.6 | T2_public_lab_standard_or_physics | architecture routing | adopt | Use distinct failure units and architecture-specific axes. | Use one normalized curve or apply fixed-tilt coefficients to trackers. | Rigid fixed-tilt pressure response and tracker aeroelastic instability are different mechanisms. | Evidence demonstrates transferable equivalence.
SWS2-C007 | Fixed-tilt preferred axis is peak transient event net-pressure demand divided by comparable qualified same-zone design net-pressure demand. | engineering_interpretation | FIXED_TILT_WIND_DESIGN_2020;ASCE_7_22;ASCE_49_21 | Browne §§1–5; ASCE provisions | T3_engineering_proxy_or_adjacent_empirical | fixed_tilt_event_to_design_net_pressure_ratio | adopt_screening | Use qualified event/design-demand calculations retaining zone and geometry; let T4 curve medians represent unresolved resistance transitions. | Treat design demand as as-built resistance, use design wind as failure D50, or claim one scalar resolves distinct module/structure capacities. | The ratio is a transparent demand normalization; separate record medians carry failure-unit resistance assumptions. | Matched failure-unit demand/capacity/disposition dataset.
SWS2-C008 | Fixed-tilt squared-speed proxy is permitted only with array-height/design gusts and named profile/aerodynamic bridges. | physics_bridge | ASCE_7_22;ASCE_49_21;NIST_THUNDERSTORM_PROFILES_2011 | ASCE wind-load basis and NIST profile study | T2_public_lab_standard_or_physics | x=(Varray/Vdesign)^2 | adopt_flagged_proxy | Use as a transparent quasi-steady screening proxy. | Use unbridged 10 m wind or interpret x as true capacity ratio. | Dynamic pressure scales with squared speed while coefficients/dynamics remain bridge-owned. | Validated transient pressure product supersedes proxy.
SWS2-C009 | Tracker preferred axis is tracker-normal local 3-second gust divided by exact-system critical-instability speed. | engineering_interpretation | PV_TRACKER_AEROELASTIC_2024;CPP_TRACKER_INSTABILITY_2015;TRACKER_LAYOUT_AEROELASTIC_2025 | benchmark §§1–3; CPP pp. 5–7; stability map | T3_engineering_proxy_or_adjacent_empirical | eta=Vnormal/Ucrit | adopt_screening | Normalize by named third-party aeroelastic qualification for the exact tracker/angle/configuration. | Supply a generic Ucrit or use fixed-tilt design speed. | Critical velocity is system, angle, layout and direction dependent. | A better qualified reduced-order demand metric is validated.
SWS2-C010 | The FM 0.75 Ucrit value is an operational stow-action flag, not a damage threshold. | source_interpretation | FM_DS_7_106_2026 | §§2.1.2.3–2.1.2.4 and §3.1 | T2_public_lab_standard_or_physics | STOW_ACTION_THRESHOLD_EXCEEDED | adopt_flag_only | Emit a control/action metadata flag at eta >= 0.75. | Force damage, force zero below 0.75, or calibrate a median from 0.75. | The source specifies action margin below tested instability speed. | FM revises the operational criterion or qualified damage data emerge.
SWS2-C011 | 1P/2P identity, qualification ID, actual angle, row position and stow/control state are required tracker context. | source_finding | IEA_PVPS_EXTREME_WEATHER_2025;TRACKER_LAYOUT_AEROELASTIC_2025;TRACKER_FIELD_MODAL_2024;FM_DS_7_106_2026 | IEA §§3.4–3.6; Frontini Fig. 7; field campaign; FM §3.1 | T2_public_lab_standard_or_physics | tracker selectors/conditioners | adopt | Preserve context and resolve numeric effects in exact-system Ucrit/bridge. | Apply universal 1P/2P, zone or stow multiplier. | Response varies with these fields but public data do not calibrate universal credits. | Qualified fleet data calibrate explicit effects.
SWS2-C012 | Unknown or confirmed stow does not select a favorable resistance scenario. | governance_decision | PV_TRACKER_DOWNBURST_2025;PV_TRACKER_AEROELASTIC_2024;FM_DS_7_106_2026 | source transfer limits and gate | T4_placeholder_or_expert_judgment | conditioner rule | adopt_fail_closed | Carry state and flags; Ucrit must already match the attained condition. | Apply current v1 0.80/1.25 multipliers or average demand before nonlinear DR. | No universal stow multiplier is supported and averaging demand before DR is mathematically biased. | Tracker-specific field calibration.
SWS2-C013 | Module and support-structure values remain separate failure units. | value_and_dependency_decision | NREL_NLR_Q1_2025_PV_BENCHMARK;VALUE_SOLAR_WORKBOOK;DOE_PV_OWNER_GUIDE_2021 | Solar_Map rows 2–3; Owner Guide §5 | T2_public_lab_standard_or_physics | four architecture-specific records | adopt | Evaluate module and structure states separately and reconcile terminal cascade. | Force module-only and structure-only outcomes into one false severity order. | The value source separates rows and observed outcomes can be alternative rather than ordered. | Matched joint state/cost data supports a better assembly.
SWS2-C014 | Module salvage after structural damage is represented by explicit T4 bounds, not a deterministic observed cascade. | engineering_dependency_rule | DOE_PV_OWNER_GUIDE_2021;SOLAR_CRITICAL_JOINTS_2025;VALENTIN_TRACKER_FAILURE_2022;NO_DIRECT_CALIBRATION_SOURCE | Owner Guide §5; critical-joint report; forensic §§3–6; bounded search log | T4_placeholder_or_expert_judgment | module salvage / destructive-collapse cascade | adopt_screening_with_bounds | Central screening treats only DS3 destructive collapse as making colocated modules nonsalvageable; also carry full-salvage and no-salvage-on-any-structure-replacement bounds. | Claim universal module destruction from structure replacement, hide salvage sensitivity, or add module replacement twice. | Field evidence supports possible cascade but not universal non-salvageability; explicit bounds expose the assumption. | Claims-level joint structural/module disposition and salvage data.
SWS2-C015 | Applying the module curve outside DS3 destructive collapse is an explicit T4 conditional-dependence assumption. | engineering_dependency_rule | NO_DIRECT_CALIBRATION_SOURCE | bounded search log and loss-assembly contract | T4_placeholder_or_expert_judgment | conditional module/structure dependence | adopt_flag_and_bounds | Carry separate state ensembles, salvage bounds and MODULE_SALVAGE_AND_CONDITIONAL_DEPENDENCE_T4_ASSUMPTION. | Claim statistical independence, a calibrated joint distribution, or an observed conditional module curve. | No matched public population supports dependence estimation. | Matched event-level joint state and salvage data.
SWS2-C016 | Foundation, power/electrical, SCADA and civil curves are withheld. | fail_closed_decision | DOE_PV_OWNER_GUIDE_2021;VALUE_SOLAR_WORKBOOK;NO_DIRECT_CALIBRATION_SOURCE | coverage audit and value rows 4–10,14 | T4_placeholder_or_expert_judgment | failure-unit coverage | withhold | Return null with stable reason codes. | Return zero or inherit module/structure DR and exposure. | Mechanism, value and exposure grains are not qualified. | Failure-unit-specific evidence and value/exposure split.
SWS2-C017 | Replacement support is allocated once outside intrinsic DR. | value_rule | VALUE_SOLAR_WORKBOOK | Solar_Map rows 12–13 and 15 | T2_public_lab_standard_or_physics | support allocation | adopt_open_rule | Allocate after direct damage with explicit claim/repair rule. | Embed in both module/structure denominators and add again downstream. | Fieldwork and inspection are repair-scope consequences, not vulnerable hardware. | Claims data establish a reusable allocation function.
SWS2-C018 | The primary reference basis is 1120 installed, 877.795702 physical, 656.981457 direct and 189.590501 support USD/kWdc in 2024 USD. | value_arithmetic | NREL_NLR_Q1_2025_PV_BENCHMARK;VALUE_SOLAR_WORKBOOK | Solar_Map rows 2–17 and summary | T2_public_lab_standard_or_physics | primary reference value basis | adopt_reference_only | Reconcile reference denominators and convert labeled contributions. | Use as site appraisal or vulnerability calibration. | The governed workbook maps the official benchmark into explicit rows. | New benchmark vintage or site valuation.
SWS2-C019 | Module plus mounting reference value is 401.204577 USD/kWdc, 45.705917% physical and 35.821837% installed. | value_arithmetic | VALUE_SOLAR_WORKBOOK | Solar_Map rows 2–3 | T2_public_lab_standard_or_physics | array reference shares | adopt_reference_only | Report array-only contribution with its denominator label. | Treat either share as an intrinsic DR cap. | Exact row arithmetic makes the value seam explicit. | Value rows or denominator change.
SWS2-C020 | Q1-2024 tracker MMP values are a sensitivity, not blended with the primary 2024 USD basis. | value_rule | NREL_Q1_2024_MMP_TRACKER | DOE Figure 1 | T2_public_lab_standard_or_physics | tracker sensitivity profile | adopt_sensitivity_only | Use module 336 and SBOS 140 together in 2023 USD for sensitivity. | Blend vintages or use the tracker profile as fixed-tilt value. | Source-native rows provide architecture cross-check but a different vintage/basis. | Benchmark reconciliation or site BOM.
SWS2-C021 | Fixed-tilt structural 90–120 2020 USD/kWdc is a range only and supplies no point default. | value_rule | NREL_Q1_2021_COST_BENCHMARK | PDF p. 27 | T2_public_lab_standard_or_physics | fixed-tilt value range | withhold_default | Use for sensitivity only when labeled. | Assign an endpoint to fixed tilt or inflate to current dollars without method. | The source combines fixed tilt and tracker and is older. | Current fixed-tilt BOM benchmark.
SWS2-C022 | All medians, beta values, zero boundaries and localized repair cost ratios are T4 screening assumptions. | parameter_tier_decision | NO_DIRECT_CALIBRATION_SOURCE | bounded search log and parameter table | T4_placeholder_or_expert_judgment | numeric curve payload | adopt_screening | Use as unweighted pressure-tested scenarios with exact provenance. | Describe as public-source-derived, fitted, probabilistic percentiles or claims-calibrated. | Public evidence constrains physics and plausible bounds but not probabilities/cost states. | Matched demand/configuration/disposition/cost data or formal elicitation.
SWS2-C023 | Fixed-tilt medians use the broad source-review envelope around design demand. | engineering_assumption | DOE_PV_OWNER_GUIDE_2021;ASCE_7_22;NO_DIRECT_CALIBRATION_SOURCE | parameter table SWS2-P018–P023 | T4_placeholder_or_expert_judgment | fixed-tilt scenario medians | adopt_screening | Treat lower/central/upper as unweighted resistance scenarios. | Interpret the values as empirical medians or code reliability. | The envelope permits below-design latent weakness and capacity beyond design without fitting sparse cases. | Matched fixed-tilt field fragility.
SWS2-C024 | Tracker medians use Ucrit-normalized broad bounds and do not use observed 16.7–28 m/s cases as literal thresholds. | engineering_assumption | IEA_PVPS_EXTREME_WEATHER_2025;VALENTIN_TRACKER_FAILURE_2022;PV_TRACKER_AEROELASTIC_2024;NO_DIRECT_CALIBRATION_SOURCE | parameter table SWS2-P024–P029 | T4_placeholder_or_expert_judgment | tracker scenario medians | adopt_screening | Use cases to pressure-test ordering and demand range only. | Fit population fragility or universal speed threshold from cases. | Case wind/configuration/value denominators are not matched or representative. | Qualified tracker population data.
SWS2-C025 | The lognormal ordered-state form is a computational surrogate, not proof of lognormal population capacity. | curve_form_decision | NO_DIRECT_CALIBRATION_SOURCE;DOE_PV_OWNER_GUIDE_2021 | curve-form decision and transfer limits | T4_placeholder_or_expert_judgment | ordered_damage_state_lognormal | adopt_screening | Produce monotone bounded state ensembles with inspectable scenarios. | Claim statistical aleatory spread or assign scenario probabilities. | The form is stable and auditable while evidence is sparse. | Population model comparison selects another form.
SWS2-C026 | The proposal is withheld above architecture-specific demand index 2.0. | governance_boundary | NO_DIRECT_CALIBRATION_SOURCE | artifact extrapolation policy | T4_placeholder_or_expert_judgment | valid_range max=2.0 | adopt_fail_closed | Reject rather than extrapolate beyond research bounds. | Clamp to one, continue extrapolation, or substitute current v1. | The elicited scenario support is not validated in the far tail. | Extreme-demand calibration or engineering review extends range.
SWS2-C027 | The current v1 workbook stow formula reads mounting_type B7 instead of stow_state B8. | legacy_audit_finding | LEGACY_SWS_V1 | current workbook Dashboard!G7 and labels B7/B8 | T4_placeholder_or_expert_judgment | legacy defect | document_do_not_patch_current | Use as a migration regression and reason for executable KATs. | Silently repair or reinterpret the current canonical artifact during this proposal. | The formula makes stow changes inert and applies probabilistic tracker treatment to fixed tilt. | Current v1 receives a separately governed patch or v2 promotion.
SWS2-C028 | Current v1 remains canonical and the proposed v2 remains absent from artifact index/changelog. | release_decision | LEGACY_SWS_V1 | current artifact/index/changelog and promotion matrix | T4_placeholder_or_expert_judgment | canonical_runtime_artifact=false | adopt | Research, validate and shadow-test without runtime cutover. | Consume proposed v2 as current or mutate v1 pin. | Major behavior/schema changes require explicit promotion. | All promotion gates pass and maintainer approves.
SWS2-C029 | Tracker DR and the FM 0.75 action flag require an exact structured event-to-qualification basis match. | engineering_contract | PV_TRACKER_AEROELASTIC_2024;TRACKER_LAYOUT_AEROELASTIC_2025;FM_DS_7_106_2026 | aeroelastic benchmark §§1–3; stability map; FM §§2.1.2.3–2.1.2.4 | T3_engineering_proxy_or_adjacent_empirical | tracker qualification-basis match | adopt_fail_closed | Match 3-second averaging, array-height tracker-normal reference, profile bridge, 1P/2P, layout, position, angle, zone and drive/lock state before evaluation. | Accept arbitrary Ucrit text, unknown attained state, or apply 0.75 across mismatched speed definitions. | Critical velocity and the action margin are system/state/speed-basis specific. | A governed certified tracker-capacity catalog supplies equivalent structured identity.
SWS2-C030 | Architecture-specific accepted input payloads are serialized and schema/validator checked. | schema_contract | ASCE_7_22;PV_TRACKER_AEROELASTIC_2024 | bundle v3 hazard-axis architecture_input_contracts | T4_placeholder_or_expert_judgment | architecture input contract | adopt | Allow a schema-aware consumer to discover fixed preferred/proxy and tracker required fields. | Rely on a nonexistent generic input field or silently fall back across architectures. | One causal pathway needs different asset-architecture axes and complete payloads. | Bundle schema gains a stronger conditional mechanism.
SWS2-C031 | Monetary loss assembly requires structured event, parent-event, zone and colocated exposure identity. | exposure_contract | DERECHO_MULTISCALE_2025;NO_DIRECT_CALIBRATION_SOURCE | artifact exposure contract and loss KAT | T4_placeholder_or_expert_judgment | colocated_common_array_zone exposure | adopt_fail_closed | Preserve identifiers and use one common fraction only when module/structure footprints are colocated. | Produce loss from values/fraction alone or force different footprints through one fraction. | Event deduplication and failure-unit exposure grain are load-bearing downstream seams. | A richer per-unit exposure contract supersedes the helper.

## Parameter_Tiers
Parameter tier table
Curve ordinates are T4 assumptions; axis/value provenance remains explicit
parameter | pathway_id | curve_id | value | param_role | tier | source_ids | reasoning | status | update_trigger
SWS2-P001 ¦ Required pathway identity | all_shared | CELL_PATHWAY_CONTRACT | straight_line_convective; no default | axis_bridge | T4_placeholder_or_expert_judgment | NWS_DOWNBURST_TAXONOMY;DERECHO_MULTISCALE_2025 | The causal wind field must be resolved before intensity evaluation. | REQUIRED_PROPOSED_CONTRACT | Governed pathway schema changes.
SWS2-P002 ¦ Fixed-tilt architecture | straight_line_convective | CELL_SELECTOR_CONTRACT | fixed_tilt_ground_mount_screening_v1 | selector_default | T3_engineering_proxy_or_adjacent_empirical | FIXED_TILT_WIND_DESIGN_2020;ASCE_7_22 | Rigid fixed-tilt ground mount is separate from aeroelastic trackers. | REQUIRED_NO_DEFAULT | Architecture-specific evidence expands supported asset classes.
SWS2-P003 ¦ Qualified tracker architecture | straight_line_convective | CELL_SELECTOR_CONTRACT | single_axis_tracker_qualified_screening_v1 | selector_default | T3_engineering_proxy_or_adjacent_empirical | PV_TRACKER_AEROELASTIC_2024;IEC_62817 | Exact-system qualification is required; generic tracker transfer is prohibited. | REQUIRED_NO_DEFAULT | Fleet calibration supports named generic archetypes.
SWS2-P004 ¦ Tracker module configuration | straight_line_convective | CELL_SELECTOR_CONTRACT | 1P or 2P; required | selector_default | T2_public_lab_standard_or_physics | IEA_PVPS_EXTREME_WEATHER_2025;TRACKER_FIELD_MODAL_2024 | Configuration is load-bearing but has no universal multiplier. | REQUIRED_CONTEXT | Exact-system Ucrit removes need to expose configuration.
SWS2-P005 ¦ Fixed preferred demand axis | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | fixed_tilt_event_to_design_net_pressure_ratio | axis_bridge | T3_engineering_proxy_or_adjacent_empirical | FIXED_TILT_WIND_DESIGN_2020;ASCE_7_22;ASCE_49_21 | Qualified event/design net-pressure-demand ratio captures zone and geometry without claiming design demand is resistance; T4 record medians represent failure-unit capacity. | ACTIVE_SCREENING_AXIS | Matched failure-unit demand/capacity/disposition data validates a better metric.
SWS2-P006 ¦ Fixed gust proxy | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | (array_height_3s_gust_mps / qualified_design_array_height_3s_gust_mps)^2 | axis_bridge | T3_engineering_proxy_or_adjacent_empirical | ASCE_7_22;NIST_THUNDERSTORM_PROFILES_2011 | Squared speed is pressure-proportional but needs named profile and demand bridges. | ACTIVE_FLAGGED_PROXY | Qualified transient pressure demand becomes available.
SWS2-P007 ¦ Tracker preferred demand axis | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | tracker_normal_3s_gust_mps / critical_instability_3s_gust_mps | axis_bridge | T3_engineering_proxy_or_adjacent_empirical | PV_TRACKER_AEROELASTIC_2024;CPP_TRACKER_INSTABILITY_2015;TRACKER_LAYOUT_AEROELASTIC_2025 | System-specific Ucrit absorbs architecture, angle and dynamic stability more honestly than design wind. | ACTIVE_SCREENING_AXIS | Validated tracker damage-demand metric replaces instability ratio.
SWS2-P008 ¦ Tracker Ucrit provenance | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | positive exact-system value plus aeroelastic_qualification_id | axis_bridge | T2_public_lab_standard_or_physics | PV_TRACKER_AEROELASTIC_2024;FM_DS_7_106_2026 | Critical speed is design/tilt/layout specific. | REQUIRED_NO_DEFAULT | Certified standardized tracker capacity catalog.
SWS2-P009 ¦ Stow action flag | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | eta >= 0.75 | conditioner_effect | T2_public_lab_standard_or_physics | FM_DS_7_106_2026 | FM action margin is preserved as metadata, not converted to damage. | FLAG_ONLY | FM criterion changes.
SWS2-P010 ¦ Tracker stow numeric credit | straight_line_convective | CELL_CONDITIONER_CONTRACT | withheld; exact attained condition belongs in Ucrit/bridge | conditioner_effect | T2_public_lab_standard_or_physics | PV_TRACKER_DOWNBURST_2025;PV_TRACKER_AEROELASTIC_2024 | No universal multiplier is supported. | WITHHELD_NO_DEFAULT | Tracker-specific event/configuration calibration.
SWS2-P011 ¦ Array zone effect | all_shared | CELL_CONDITIONER_CONTRACT | metadata or resolved in qualified demand; no downstream multiplier | conditioner_effect | T2_public_lab_standard_or_physics | FIXED_TILT_WIND_DESIGN_2020;TRACKER_LAYOUT_AEROELASTIC_2025 | Perimeter/interior position changes loads but double application is prohibited. | BRIDGE_OWNED | Qualified universal zonal modifier with non-overlap proof.
SWS2-P012 ¦ Fastener/clamp condition effect | all_shared | CELL_CONDITIONER_CONTRACT | metadata only; no favorable scenario selection | conditioner_effect | T2_public_lab_standard_or_physics | DOE_PV_OWNER_GUIDE_2021;SOLAR_CRITICAL_JOINTS_2025 | Condition is important but uncalibrated. | UNCALIBRATED_CONTEXT | Field population links condition to state probabilities.
SWS2-P013 ¦ Fixed valid range | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | 0.0 to 2.0; flag >1.6 | extrapolation_guard | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Research support is insufficient beyond the broad elicited range. | WITHHOLD_ABOVE_MAX | Independent engineering review extends support.
SWS2-P014 ¦ Tracker valid range | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.0 to 2.0; flag >1.7 | extrapolation_guard | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Qualified instability ratio remains a screening axis, not a far-tail theorem. | WITHHOLD_ABOVE_MAX | Extreme tracker event/structural data.
SWS2-P015 ¦ Hard zero boundary | all_shared | ALL_FOUR_CURVES | x < 0.10 returns DS0 | curve_shape | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Numerical stability/governance boundary only; not an evidence-based no-damage theorem. | ACTIVE_SCREENING_ASSUMPTION | Observed low-demand damage or formal elicitation.
SWS2-P016 ¦ Module localized cost ratio | all_shared | SWS2_SLC_FIXED_MODULE_ORDERED_STATES¦SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.10 of same failure-unit value | value_mapping | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Transparent bounded repair proxy; prevention premiums are not used as repair cost. | ACTIVE_SCREENING_ASSUMPTION | Claims repair scope/cost distribution.
SWS2-P017 ¦ Structure localized cost ratio | all_shared | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES¦SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 0.15 of same failure-unit value | value_mapping | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Transparent bounded repair proxy for local joints/rails/drive work. | ACTIVE_SCREENING_ASSUMPTION | Claims repair scope/cost distribution.
SWS2-P018 ¦ Fixed module beta_ln | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | 0.30 | curve_shape | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Sensitivity-only smoothing within a broad unweighted envelope. | ACTIVE_SCREENING_ASSUMPTION | Population fragility or formal elicitation.
SWS2-P019 ¦ Fixed module lower medians | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | [0.65, 1.20] | curve_shape | T4_placeholder_or_expert_judgment | DOE_PV_OWNER_GUIDE_2021;NO_DIRECT_CALIBRATION_SOURCE | Allows latent joint weakness below design and major replacement beyond design. | ACTIVE_SCREENING_ASSUMPTION | Matched fixed-tilt event data.
SWS2-P020 ¦ Fixed module central medians | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | [0.85, 1.55] | curve_shape | T4_placeholder_or_expert_judgment | ASCE_7_22;NO_DIRECT_CALIBRATION_SOURCE | Centers a screening scenario around design demand without treating code as failure capacity. | ACTIVE_SCREENING_ASSUMPTION | Matched fixed-tilt event data.
SWS2-P021 ¦ Fixed module upper medians | straight_line_convective | SWS2_SLC_FIXED_MODULE_ORDERED_STATES | [1.05, 1.95] | curve_shape | T4_placeholder_or_expert_judgment | DOE_FEMP_STORM_HARDENING_2020;NO_DIRECT_CALIBRATION_SOURCE | Represents stronger qualified systems; hardening costs do not calibrate the values. | ACTIVE_SCREENING_ASSUMPTION | Matched hardened-system data.
SWS2-P022 ¦ Fixed structure beta_ln | straight_line_convective | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | 0.30 | curve_shape | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Sensitivity-only smoothing. | ACTIVE_SCREENING_ASSUMPTION | Population fragility or formal elicitation.
SWS2-P023 ¦ Fixed structure medians by scenario | straight_line_convective | SWS2_SLC_FIXED_STRUCTURE_ORDERED_STATES | lower [0.90,1.20,1.50]; central [1.15,1.55,1.90]; upper [1.45,1.95,2.35] | curve_shape | T4_placeholder_or_expert_judgment | DOE_PV_OWNER_GUIDE_2021;ASCE_7_22;NO_DIRECT_CALIBRATION_SOURCE | Separates local repair, structure replacement with module salvage, and destructive-collapse/non-salvage states. | ACTIVE_SCREENING_ASSUMPTION | Matched structural/module disposition and salvage data.
SWS2-P024 ¦ Tracker module beta_ln | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | 0.275 | curve_shape | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Within the science-review sensitivity range; no statistical interpretation. | ACTIVE_SCREENING_ASSUMPTION | Population tracker fragility or formal elicitation.
SWS2-P025 ¦ Tracker module medians by scenario | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES | lower [0.80,1.15]; central [0.95,1.40]; upper [1.10,1.70] | curve_shape | T4_placeholder_or_expert_judgment | IEA_PVPS_EXTREME_WEATHER_2025;PV_TRACKER_AEROELASTIC_2024;NO_DIRECT_CALIBRATION_SOURCE | Broad Ucrit-normalized module-retention scenarios constrained but not fitted by field cases. | ACTIVE_SCREENING_ASSUMPTION | Qualified event/configuration/disposition dataset.
SWS2-P026 ¦ Tracker structure beta_ln | straight_line_convective | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 0.275 | curve_shape | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | Sensitivity-only smoothing; no population beta claim. | ACTIVE_SCREENING_ASSUMPTION | Population tracker fragility or formal elicitation.
SWS2-P027 ¦ Tracker structure medians by scenario | straight_line_convective | SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | lower [0.95,1.15,1.35]; central [1.15,1.40,1.65]; upper [1.35,1.70,2.00] | curve_shape | T4_placeholder_or_expert_judgment | IEA_PVPS_EXTREME_WEATHER_2025;PV_TRACKER_DOWNBURST_2025;PV_TRACKER_AEROELASTIC_2024;NO_DIRECT_CALIBRATION_SOURCE | Broad Ucrit-normalized local repair, structure-replacement and destructive-collapse states; evidence supplies mechanism not probability. | ACTIVE_SCREENING_ASSUMPTION | Qualified event/configuration/disposition/salvage dataset.
SWS2-P028 ¦ Module salvage / destructive-collapse cascade | all_shared | LOSS_ASSEMBLY_CONTRACT | central: DS3 destructive collapse makes modules nonsalvageable; bounds: full salvage to no salvage on any structure replacement | dependency_rule | T4_placeholder_or_expert_judgment | DOE_PV_OWNER_GUIDE_2021;VALENTIN_TRACKER_FAILURE_2022;SOLAR_CRITICAL_JOINTS_2025;NO_DIRECT_CALIBRATION_SOURCE | Observed cases support possible cascade, not universal non-salvage; explicit bounds expose the T4 assumption. | ACTIVE_SCREENING_WITH_BOUNDS | Claims-level joint-state and salvage evidence.
SWS2-P029 ¦ Conditional module/structure dependence | all_shared | LOSS_ASSEMBLY_CONTRACT | module curve applied conditional on no DS3 under a flagged T4 assumption | dependency_rule | T4_placeholder_or_expert_judgment | NO_DIRECT_CALIBRATION_SOURCE | No joint population supports correlation or conditional probabilities. | LIMITATION_FLAG_AND_BOUNDS | Matched joint module/structure state data.
SWS2-P030 ¦ Module reference value | all_shared | VALUE_LINKAGE | 291.21485143992487 2024 USD/kWdc; informational, explicit site value required | value_mapping | T2_public_lab_standard_or_physics | NREL_NLR_Q1_2025_PV_BENCHMARK;VALUE_SOLAR_WORKBOOK | Row-complete repository reference; not an implicit default. | REFERENCE_ONLY | Benchmark vintage or site BOM changes.
SWS2-P031 ¦ Mounting reference value | all_shared | VALUE_LINKAGE | 109.98972602739727 2024 USD/kWdc; tracker/fixed transfer limited | value_mapping | T2_public_lab_standard_or_physics | NREL_NLR_Q1_2025_PV_BENCHMARK;VALUE_SOLAR_WORKBOOK | Repository reference row cannot support a finer structural split. | REFERENCE_ONLY | Architecture-specific current BOM benchmark.
SWS2-P032 ¦ Fixed structural value | straight_line_convective | VALUE_LINKAGE | explicit site value required; 90–120 2020 USD/kWdc range sensitivity only | value_mapping | T2_public_lab_standard_or_physics | NREL_Q1_2021_COST_BENCHMARK | Older combined-architecture range is inadequate for a point default. | NO_IMPLICIT_DEFAULT | Current fixed-tilt BOM benchmark.
SWS2-P033 ¦ Tracker sensitivity values | straight_line_convective | VALUE_LINKAGE | 336 module + 140 SBOS 2023 USD/kWdc; do not blend | value_mapping | T2_public_lab_standard_or_physics | NREL_Q1_2024_MMP_TRACKER | Source-native tracker MMP cross-check with a different vintage. | SENSITIVITY_ONLY | New source-native tracker benchmark.
SWS2-P034 ¦ Replacement support | all_shared | VALUE_LINKAGE | 189.59050092005714 2024 USD/kWdc reference pool; allocate once | value_mapping | T2_public_lab_standard_or_physics | VALUE_SOLAR_WORKBOOK | Support follows repair scope and is not vulnerable hardware. | ALLOCATION_RULE_OPEN | Claims-based allocation function.
SWS2-P035 ¦ Tracker qualification-basis match | straight_line_convective | SWS2_SLC_TRACKER_MODULE_ORDERED_STATES¦SWS2_SLC_TRACKER_SBOS_ORDERED_STATES | 3 s + array-height tracker-normal + profile + 1P/2P + layout + position + angle + zone + drive/lock exact match | axis_bridge | T3_engineering_proxy_or_adjacent_empirical | PV_TRACKER_AEROELASTIC_2024;TRACKER_LAYOUT_AEROELASTIC_2025;FM_DS_7_106_2026 | Ucrit and FM action margin are valid only for the matched system/state/speed definition. | REQUIRED_FAIL_CLOSED | Certified structured tracker qualification catalog.
SWS2-P036 ¦ Colocated exposure object | all_shared | LOSS_ASSEMBLY_CONTRACT | event_id + parent_convective_event_id + array_zone_id_or_group + colocated_common_array_zone + exposed_fraction | exposure_or_value | T4_placeholder_or_expert_judgment | DERECHO_MULTISCALE_2025;NO_DIRECT_CALIBRATION_SOURCE | Identifiers prevent event/zone double count; one fraction is valid only for explicitly colocated module/structure footprints. | REQUIRED_FOR_LOSS_NO_DEFAULT | Per-unit exposure objects supersede common-zone helper.

## Legacy_Comparison
Legacy v1 versus proposed v2 audit
Different axes, units, values and dependency rules: numerical equality is not a regression target
case_id | illustrative_gust_mph | illustrative_design_gust_mph | current_v1_effective_demand | current_v1_default_loss_usd_100_mwdc | proposed_v2_fixed_pressure_index | proposed_v2_lower_loss_usd_100_mwdc | proposed_v2_central_loss_usd_100_mwdc | proposed_v2_upper_loss_usd_100_mwdc | comparison_status | guardrail
AUDIT_100 | 100 | 120 | 0.728732638888889 | 938229.7861309352 | 0.6944444444444445 | 3379550.7793642418 | 948757.1821398379 | 267500.27905569173 | different_models_and_denominators | V1 uses its defective default stow routing, zone 1.15 and five shares; v2 uses fixed-tilt array reference rows and the central T4 DS3 non-salvage rule. Not a regression target.
AUDIT_120 | 120 | 120 | 1.049375 | 14167049.099062802 | 1.0 | 15108385.188678259 | 5554020.373892352 | 1968648.4823629744 | different_models_and_denominators | Illustrative event/design demand ratio only; a real v2 call requires a qualified convective pressure bridge. Salvage bounds are reported separately by the helper.
AUDIT_140 | 140 | 120 | 1.4283159722222225 | 32945630.993683267 | 1.3611111111111114 | 31273944.338243395 | 18091105.377158877 | 7954134.798822228 | different_models_and_denominators | Resistance scenarios are unweighted and not confidence intervals; module-salvage bounds are an additional T4 dimension.
AUDIT_160 | 160 | 120 | 1.8655555555555554 | 35685658.959134795 | 1.7777777777777777 | 38500451.041043974 | 31972286.428077072 | 20399288.98319297 | different_models_and_denominators | V2 covers module+mounting only; withheld units remain incomplete.

## QA_Checks
Formula-driven quality checks
All release-critical checks must be PASS; promotion remains blocked for scientific/consumer gates
Check | Formula / value | Expected | Result | Meaning
Curve rows | 12 | 12 | PASS | 4 records × 3 scenarios
Source rows | 29 | 29 | PASS | Bounded evidence register
Claim rows | 31 | 31 | PASS | Claim provenance coverage
Parameter rows | 36 | 36 | PASS | Parameter tier coverage
Runtime KAT count | 6 | 6 | PASS | Equation and withholding tests
Rejection count | 16 | 16 | PASS | Fail-closed contract
Loss rejection KAT count | 4 | 4 | PASS | Atomic value/exposure contract
Consumer pin KAT count | 4 | 4 | PASS | Exact model/docs/schema/SHA binding
Primary direct hardware | 656.9815 | 656.9815 | PASS | 2024 USD/kWdc
Primary support | 189.5905 | 189.5905 | PASS | Allocated once
Primary physical | 877.7957 | 877.7957 | PASS | Direct + support + civil
Installed | 1120 | 1120 | PASS | Physical + excluded
Fixed x=1 central module DR | 0.13543 | 0.13543 | PASS | Independent equation KAT
Tracker eta=1 central structure DR | 0.13983 | 0.13983 | PASS | Independent equation KAT

## Dashboard
Convective wind × utility solar — proposal dashboard
Screening model only · choose architecture-specific qualified demand · no hurricane/tornado fallback
Model | Pathway | Lifecycle | Promotion
model v2.0 / docs r1 | straight_line_convective | proposed noncanonical | BLOCKED
Architecture | Preferred axis | Numeric units | Critical qualification
Rigid fixed tilt | event/design net-pressure demand | module + support structure | named transient aerodynamic bridge; T4 capacity medians
Qualified single-axis tracker | tracker-normal gust / exact-system Ucrit | module + tracker SBOS | 1P/2P + exact test/model + angle/state
Key fixed x=1 result | Lower | Central | Upper
Module DR | 0.33696 | 0.13543 | 0.055244
Structure DR | 0.32652 | 0.10932 | 0.027217
Reference 25%-exposed central-T4 direct array loss | 37.771 | 13.8851 | 4.9216
Value boundary: module + mounting reference = 401.204577 USD/kWdc = 45.705917% of physical = 35.821837% of installed. These are labeled contributions, never intrinsic DR caps.